## History
Version | Date | Revised by | Reviewed by | Description
V1.0.0 | 2025-05-08 | OPJ |  | 重新梳理，初版，base版本是MIC_自研版本点表。
V1.0.1 | 2025-08-14 | xuc01 |  | 1. History: 优化格式，版本号与其他通讯表格匹配 A0->V1.0.1 2. 寄存器分布： sheet“目录”更名为“寄存器分布”； 输入寄存器-簇信息长度 2991->3000； 起始地址改为由公式计算; 3. 格式梳理： 字段列需包含中文名/英文名； 删除非必要列(重点测试关注、BMS2.0平台开发需求等)； 列名改为英文； 4. 离散输入寄存器： 堆数据信息：81-121补充M核检测的未上报至EMS的故障； 簇数据信息：246-255/297-350补充三级架构RBMS未上报至EMS的故障； 簇数据信息：351-366补充二级架构RBMS未上报至EMS的故障； 列“Mapping Signal BMS20/21”：用于标注BMS20(三级架构)/BMS21(二级架构)平台mapping的信号 5. 保持寄存器： 将保留的点位更新为“预留 Reserved” 保持寄存器当前未实现任何功能mapping，需基于需求进行开发，新增列“Mapping Signal BMS20/21” 6. 输入寄存器： 将保留的点位更新为“预留 Reserved”，并将“预留 Reserved”内容调整至集中放置 新增列“Mapping Signal BMS20/21” 簇信息数据分类(以簇1为例)：100-200 概要信息，201-2200 详细信息，2201-3000 软件debug信息(由软件自行维护) 7. 删除sheet“问题列表” 8. 修改电表信息-总有功功率、电表信息-总无功功率数据类型 9. 更新簇编号与数组编号的描述形式
V1.0.2 | 2025-09-22 | zhangyf03 |  | 输入寄存器： 1. Bank：最高/低/平均温度分辨率 1->0.1；堆连接失败原因Remark描述更新； 2. Rack：最高/低/平均单体温度分辨率1->0.1；最高/低/平均极柱温度Mapping Signal BMS20信号名称更新；高压箱温度T0-T3分辨率1->0.1；绝缘禁止原因Remark描述更新；
V1.0.3 | 2025-09-25 | xuc01 |  | 输入寄存器: Bank: 将重复的堆最近一次放电电量改为Reserved
V1.0.4 | 2025-09-28 | xuc01 |  | 离散输入寄存器： 至少一个簇的CAN通讯丢失告警 Signal Source：RBMS_Fault_Data -> BBMS_Fault_Data
V1.0.5 | 2025-09-28 | liaozc |  | 输入寄存器： 修改列“Mapping Signal BMS20” -> “Mapping Signal BMS20/BMS23” 离散输入寄存器： 1.“簇 (i+1) 消防重度告警”出现重复，故修改266行“簇 (i+1) 消防重度告警” -> “簇 (i+1) 气溶胶2告警” 2.新增285-290行故障 3.新增列”Mapping Signal BMS23“
V1.0.6 | 2025-10-10 | liaozc |  | 输入寄存器： 1.删除列“Mapping Signal BMS21” 离散输入寄存器： 1.删除列“Mapping Signal BMS21” 2.修改列“Mapping Signal BMS23”中“/”使用空格代替
V1.0.7 | 2025-11-05 | lijy06 |  | 输入寄存器： 1.新增充电电压限制、放电电压限制、SOP、bms状态
V1.0.8 | 2025-11-19 | lijy06 |  | 离散输入寄存器： 1.市电异常告警修改为市电异常重度告警，mapping信号由BBMS_EMCR_POWER_SUPPLY_ABNORMAL_FAULT修改为BBMS_EMCR_POWER_SUPPLY_ABNORMAL_LEVEL1_FAULT 2.新增市电异常轻度告警
V1.0.9 | 2025-11-25 | lihw |  | 簇 (i+1) PACK连接器温度(j+1)的Classification：PoleT-Array → ConnectT-Array
V1.0.10 | 2025-12-02 | lijy06 |  | 离散输入寄存器： 1.除湿机通讯节点丢失告警描述修改为电池舱除湿机通讯节点丢失告警，mapping信号由BBMS_EMCR_DEHUMIDIFIER_TO_BMS_COMMUNICATION_LOST_FAULT修改为BBMS_EMCR_BATTERYCABIN_DEHUMIDIFIER_TO_BMS_COMM_LOST_FAULT
V1.0.11 | 2025-12-02 | xuc01 |  | 输入寄存器： 簇 (i+1) PACK连接器温度(j+1)，start address: i * 3000 + 1701 + j → i * 3000 + 1761 + j
V1.0.12 | 2025-12-24 | xuc01 |  | 输入寄存器： 簇 (i+1) 工作状态 String (i+1) Status，start address: i * 3000 + 144
V1.0.13 | 2026-01-29 | xuc01 |  | 新增： 1. 特殊说明 2. 标注保持寄存器中未实现的功能

## 特殊说明与寄存器分布
特殊说明： 1. 适用范围 本表为 BMS 2.0 / BMS 2.3 三级架构平台点表。 其中，BMS 2.3 平台代表项目为：418 户外柜组成的三级架构系统。 外设相关点表 单独维护，不在本表中体现具体点位信息。 2. Mapping 方式说明 自动化 Mapping：离散输入寄存器、输入寄存器 手动 Mapping：保持寄存器 3. 点位 Mapping 判定规则 对于 离散输入寄存器 和 输入寄存器： 若需确认某点位是否在对应平台（BMS 2.0 / BMS 2.3）存在 Mapping 信号，请查看 “Mapping Signal BMS20” 或 “Mapping Signal BMS23” 列。 若对应列 无 Mapping 信号，则表示该点位 无法读取到有效数据。 4. 随固件发布文件说明 随固件释放的 摩尔信使文件 仅包含 自动化 Mapping 的寄存器，即：离散输入寄存器、输入寄存器。 5. 版本变更标识规则 每次版本更新时，仅对相较上一版本发生变化的内容进行黄色高亮标识。
离散输入寄存器表 / Discrete Input Register Table
名称 / Name | 起始地址(十进制) / Start address (decimal) | 总长度 / Total length
堆数据信息/System data information | 1 | 199
簇 1 数据信息/String 1 data informaton | 200 | 200
簇 2 数据信息/String 2 data informaton | 400 | 200
簇 3 数据信息/String 3 data informaton | 600 | 200
簇 4 数据信息/String 4 data information | 800 | 200
簇 5 数据信息/String 5 data information | 1000 | 200
簇 6 数据信息/String 6 data information | 1200 | 200
簇 7 数据信息/String 7 data information | 1400 | 200
簇 8 数据信息/String 8 data information | 1600 | 200
…… | … | …
保持寄存器表 / Holding register table
名称 / Name | 起始地址(十进制) / Start address (decimal) | 总长度 / Total length
项目控制和配置信息/Project control and configuration information | 500 | 200
输入寄存器表 / Input register table
名称 / Name | 起始地址(十进制) / Start address (decimal) | 总长度 / Total length
堆数据信息/System data information | 1 | 99
簇 1 数据信息/String 1 data information | 100 | 3000
簇 2 数据信息/String 2 data information | 3100 | 3000
簇 3 数据信息/String 3 data information | 6100 | 3000
簇 4 数据信息/String 4 data information | 9100 | 3000
簇 5 数据信息/String 5 data information | 12100 | 3000
簇 6 数据信息/String 6 data information | 15100 | 3000
簇 7 数据信息/String 7 data information | 18100 | 3000
簇 8 数据信息/String 8 data information | 21100 | 3000
…… | … | …
外设信息/ Project peripheral information | 60100 | 1500

## 离散输入寄存器
Field | Start address (decimal) | DataType | Bit Length (Bit) | Resolution | offset | Unit | Remark | Layer | Classification | Signal Source | Mapping Signal BMS20 | Mapping Signal BMS23
堆内各组端电压欠压轻度告警汇总 Summary of total voltage undervoltage slight alarm at each string | 1 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_HVSH_BATTERY_UNDER_VOLTAGE_LEVEL3_FAULT | RBMS_HVSH_BATTERY_UNDER_VOLTAGE_LEVEL3_FAULT
堆内各组端电压欠压中度告警汇总 Summary of total voltage undervoltage medium alarm at each string | 2 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_HVSH_BATTERY_UNDER_VOLTAGE_LEVEL2_FAULT | RBMS_HVSH_BATTERY_UNDER_VOLTAGE_LEVEL2_FAULT
堆内各组端电压欠压重度告警汇总 Summary of total voltage undervoltage serious alarm at each string | 3 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_HVSH_BATTERY_UNDER_VOLTAGE_LEVEL1_FAULT | RBMS_HVSH_BATTERY_UNDER_VOLTAGE_LEVEL1_FAULT
堆内各组端电压过压轻度告警汇总 Summary of total voltage overvoltage slight alarm at each string | 4 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_HVSH_BATTERY_OVER_VOLTAGE_LEVEL3_FAULT | RBMS_HVSH_BATTERY_OVER_VOLTAGE_LEVEL3_FAULT
堆内各组端过压过压中度告警汇总 Summary of total voltage overvoltage medium alarm at each string | 5 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_HVSH_BATTERY_OVER_VOLTAGE_LEVEL2_FAULT | RBMS_HVSH_BATTERY_OVER_VOLTAGE_LEVEL2_FAULT
堆内各组端过压过压重度告警汇总 Summary of total voltage overvoltage serious alarm at each string | 6 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_HVSH_BATTERY_OVER_VOLTAGE_LEVEL1_FAULT | RBMS_HVSH_BATTERY_OVER_VOLTAGE_LEVEL1_FAULT
堆内各组端充电过流轻度告警汇总 Summary of charge overcurrent slight alarm at each string | 7 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_BTCD_RECHARGE_OVER_CURRENT_LEVEL3_FAULT | RBMS_BTCD_RECHARGE_OVER_CURRENT_LEVEL3_FAULT
堆内各组端充电过流中度告警汇总 Summary of charge overcurrent medium alarm at each string | 8 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_BTCD_RECHARGE_OVER_CURRENT_LEVEL2_FAULT | RBMS_BTCD_RECHARGE_OVER_CURRENT_LEVEL2_FAULT
堆内各组端充电过流重度告警汇总 Summary of charge overcurrent serious alarm at each string | 9 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_BTCD_RECHARGE_OVER_CURRENT_LEVEL1_FAULT | RBMS_BTCD_RECHARGE_OVER_CURRENT_LEVEL1_FAULT
堆内各组端放电过流轻度告警汇总 Summary of discharge overcurrent slight alarm at each string | 10 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_BTCD_DISCHARGE_OVER_CURRENT_LEVEL3_FAULT | RBMS_BTCD_DISCHARGE_OVER_CURRENT_LEVEL3_FAULT
堆内各组端放电过流中度告警汇总 Summary of discharge overcurrent medium alarm at each string | 11 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_BTCD_DISCHARGE_OVER_CURRENT_LEVEL2_FAULT | RBMS_BTCD_DISCHARGE_OVER_CURRENT_LEVEL2_FAULT
堆内各组端放电过流重度告警汇总 Summary of discharge overcurrent serious alarm at each string | 12 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_BTCD_DISCHARGE_OVER_CURRENT_LEVEL1_FAULT | RBMS_BTCD_DISCHARGE_OVER_CURRENT_LEVEL1_FAULT
堆内各组绝缘电阻低轻度告警汇总 Summary of low insulation resistance slight alarm at each string | 13 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_ISOH_ISOLATION_LOW_LEVEL3_FAULT | RBMS_ISOH_ISOLATION_LOW_LEVEL3_FAULT
堆内各组绝缘电阻低中度告警汇总 Summary of low insulation resistance medium alarm at each string | 14 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_ISOH_ISOLATION_LOW_LEVEL2_FAULT | RBMS_ISOH_ISOLATION_LOW_LEVEL2_FAULT
堆内各组绝缘电阻低重度告警汇总 Summary of low insulation resistance serious alarm at each string | 15 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_ISOH_ISOLATION_LOW_LEVEL1_FAULT | RBMS_ISOH_ISOLATION_LOW_LEVEL1_FAULT
堆内各单体过压轻度告警汇总 Summary of cell over voltage slight alarm at each string | 16 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLVH_MAXCELLV_OV_LEVEL3_FAULT | RBMS_CLVH_MAXCELLV_OV_LEVEL3_FAULT
堆内各单体过压中度告警汇总 Summary of cell over voltage medium alarm at each string | 17 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLVH_MAXCELLV_OV_LEVEL2_FAULT | RBMS_CLVH_MAXCELLV_OV_LEVEL2_FAULT
堆内各单体过压重度告警汇总 Summary of cell over voltage serious alarm at each string | 18 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLVH_MAXCELLV_OV_LEVEL1_FAULT | RBMS_CLVH_MAXCELLV_OV_LEVEL1_FAULT
堆内各单体欠压轻度告警汇总 Summary of cell low voltage slight alarm at each string | 19 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLVH_MINCELLV_UV_LEVEL3_FAULT | RBMS_CLVH_MINCELLV_UV_LEVEL3_FAULT
堆内各单体欠压中度告警汇总 Summary of cell low voltage medium alarm at each string | 20 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLVH_MINCELLV_UV_LEVEL2_FAULT | RBMS_CLVH_MINCELLV_UV_LEVEL2_FAULT
堆内各单体欠压重度告警汇总 Summary of cell low voltage serious alarm at each string | 21 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLVH_MINCELLV_UV_LEVEL1_FAULT | RBMS_CLVH_MINCELLV_UV_LEVEL1_FAULT
堆内各单体压差轻度告警汇总 Summary of cell differential voltage slight alarm at each string | 22 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLVH_DELTACELLV_OL_LEVEL3_FAULT | RBMS_CLVH_DELTACELLV_OL_LEVEL3_FAULT
堆内各单体压差中度告警汇总 Summary of cell differential voltage medium alarm at each string | 23 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLVH_DELTACELLV_OL_LEVEL2_FAULT | RBMS_CLVH_DELTACELLV_OL_LEVEL2_FAULT
堆内各单体压差重度告警汇总 Summary of cell differential voltage serious alarm at each string | 24 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLVH_DELTACELLV_OL_LEVEL1_FAULT | RBMS_CLVH_DELTACELLV_OL_LEVEL1_FAULT
堆内各单体充电欠温轻度告警汇总 Summary of cell charge low temperature slight alarm at each string | 25 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLTH_CHG_UNDER_TEMPERATURE_LEVEL3_FAULT | RBMS_CLTH_CHG_UNDER_TEMPERATURE_LEVEL3_FAULT
堆内各单体充电欠温中度告警汇总 Summary of cell charge low temperature medium alarm at each string | 26 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLTH_CHG_UNDER_TEMPERATURE_LEVEL2_FAULT | RBMS_CLTH_CHG_UNDER_TEMPERATURE_LEVEL2_FAULT
堆内各单体充电欠温重度告警汇总 Summary of cell charge low temperature serious alarm at each string | 27 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLTH_CHG_UNDER_TEMPERATURE_LEVEL1_FAULT | RBMS_CLTH_CHG_UNDER_TEMPERATURE_LEVEL1_FAULT
堆内各单体充电过温轻度告警汇总 Summary of cell charge over temperature slight alarm at each string | 28 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLTH_CHG_OVER_TEMPERATURE_LEVEL3_FAULT | RBMS_CLTH_CHG_OVER_TEMPERATURE_LEVEL3_FAULT
堆内各单体充电过温中度告警汇总 Summary of cell charge over temperature medium alarm at each string | 29 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLTH_CHG_OVER_TEMPERATURE_LEVEL2_FAULT | RBMS_CLTH_CHG_OVER_TEMPERATURE_LEVEL2_FAULT
堆内各单体充电过温重度告警汇总 Summary of cell charge over temperature serious alarm at each string | 30 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLTH_CHG_OVER_TEMPERATURE_LEVEL1_FAULT | RBMS_CLTH_CHG_OVER_TEMPERATURE_LEVEL1_FAULT
堆内各单体放电欠温轻度告警汇总 Summary of cell discharge low temperature slight alarm at each string | 31 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLTH_DSG_UNDER_TEMPERATURE_LEVEL3_FAULT | RBMS_CLTH_DSG_UNDER_TEMPERATURE_LEVEL3_FAULT
堆内各单体放电欠温中度告警汇总 Summary of cell discharge low temperature medium alarm at each string | 32 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLTH_DSG_UNDER_TEMPERATURE_LEVEL2_FAULT | RBMS_CLTH_DSG_UNDER_TEMPERATURE_LEVEL2_FAULT
堆内各单体放电欠温重度告警汇总 Summary of cell discharge low temperature serious alarm at each string | 33 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLTH_DSG_UNDER_TEMPERATURE_LEVEL1_FAULT | RBMS_CLTH_DSG_UNDER_TEMPERATURE_LEVEL1_FAULT
堆内各单体放电过温轻度告警汇总 Summary of cell discharge over temperature slight alarm at each string | 34 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLTH_DSG_OVER_TEMPERATURE_LEVEL3_FAULT | RBMS_CLTH_DSG_OVER_TEMPERATURE_LEVEL3_FAULT
堆内各单体放电过温中度告警汇总 Summary of cell discharge over temperature medium alarm at each string | 35 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLTH_DSG_OVER_TEMPERATURE_LEVEL2_FAULT | RBMS_CLTH_DSG_OVER_TEMPERATURE_LEVEL2_FAULT
堆内各单体放电过温重度告警汇总 Summary of cell discharge over temperature serious alarm at each string | 36 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLTH_DSG_OVER_TEMPERATURE_LEVEL1_FAULT | RBMS_CLTH_DSG_OVER_TEMPERATURE_LEVEL1_FAULT
堆内各单体温差轻度告警汇总 Summary of cell differential temperature slight alarm at each string | 37 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLTH_DELTA_TEMPERATURE_TOO_MUCH_LEVEL3_FAULT | RBMS_CLTH_DELTA_TEMPERATURE_TOO_MUCH_LEVEL3_FAULT
堆内各单体温差中度告警汇总 Summary of cell differential temperature medium alarm at each string | 38 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLTH_DELTA_TEMPERATURE_TOO_MUCH_LEVEL2_FAULT | RBMS_CLTH_DELTA_TEMPERATURE_TOO_MUCH_LEVEL2_FAULT
堆内各单体温差重度告警汇总 Summary of cell differential temperature serious alarm at each string | 39 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLTH_DELTA_TEMPERATURE_TOO_MUCH_LEVEL1_FAULT | RBMS_CLTH_DELTA_TEMPERATURE_TOO_MUCH_LEVEL1_FAULT
堆内各单体 SOC 低轻度告警汇总 Summary of cell SOC low slight alarm at each string | 40 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_SOCA_SOC_TOO_LOW_LEVEL3_FAULT | RBMS_SOCA_SOC_TOO_LOW_LEVEL3_FAULT
堆内各单体 SOC 低中度告警汇总 Summary of cell SOC low medium alarm at each string | 41 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_SOCA_SOC_TOO_LOW_LEVEL2_FAULT | RBMS_SOCA_SOC_TOO_LOW_LEVEL2_FAULT
堆内各单体 SOC 低重度告警汇总 Summary of cell SOC low serious alarm at each string | 42 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_SOCA_SOC_TOO_LOW_LEVEL1_FAULT | RBMS_SOCA_SOC_TOO_LOW_LEVEL1_FAULT
堆内各单体 SOC 高轻度告警汇总 Summary of cell SOC high slight alarm at each string | 43 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_SOCA_SOC_TOO_HIGH_LEVEL3_FAULT | RBMS_SOCA_SOC_TOO_HIGH_LEVEL3_FAULT
堆内各单体 SOC 高中度告警汇总 Summary of cell SOC high medium alarm at each string | 44 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_SOCA_SOC_TOO_HIGH_LEVEL2_FAULT | RBMS_SOCA_SOC_TOO_HIGH_LEVEL2_FAULT
堆内各单体 SOC 高重度告警汇总 Summary of cell SOC high serious alarm at each string | 45 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_SOCA_SOC_TOO_HIGH_LEVEL1_FAULT | RBMS_SOCA_SOC_TOO_HIGH_LEVEL1_FAULT
堆内各单体 SOH 低轻度告警汇总 Summary of cell SOH low slight alarm at each string | 46 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_SOHA_SOH_TOO_LOW_LEVEL3_FAULT | RBMS_SOHA_SOH_TOO_LOW_LEVEL3_FAULT
堆内各单体 SOH 低中度告警汇总 Summary of cell SOH low medium alarm at each string | 47 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_SOHA_SOH_TOO_LOW_LEVEL2_FAULT | RBMS_SOHA_SOH_TOO_LOW_LEVEL2_FAULT
堆内各单体 SOH 低重度告警汇总 Summary of cell SOH low serious alarm at each string | 48 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_SOHA_SOH_TOO_LOW_LEVEL1_FAULT | RBMS_SOHA_SOH_TOO_LOW_LEVEL1_FAULT
堆内各主控失联汇总 Summary of ESBCM lost communicaion alarm at each string | 49 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_EMCR_ONERACK_TO_BANK_COMMUNICATION_LOST_FAULT | BBMS_EMCR_ONERACK_TO_BANK_COMMUNICATION_LOST_FAULT
堆内各从控失联汇总 Summary of ESBMM lost communicaion alarm at each string | 50 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_AFES_DAISY_CHAIN_MULTIPLE_POINT_OFF_FAULT | RBMS_AFES_DAISY_CHAIN_MULTIPLE_POINT_OFF_FAULT
堆内组间电压差异过大告警 Abnormal voltage difference between strings alarm | 51 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_BCFR_EXCESSIVE_VOLTAGE_DIFF_FAULT | BBMS_BCFR_EXCESSIVE_VOLTAGE_DIFF_FAULT
堆内主正继电器断开告警汇总 Summary of main positive contactor stuck open alarm at each string | 52 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CTSC_MAIN_POSITIVE_RELAY_STUCK_OPEN_FAULT | RBMS_CTSC_MAIN_POSITIVE_RELAY_STUCK_OPEN_FAULT
堆内主负继电器断开告警汇总 Summary of main negative contactor stuck open alarm at each string | 53 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CTSC_MAIN_NEGATIVE_RELAY_STUCK_OPEN_FAULT | RBMS_CTSC_MAIN_NEGATIVE_RELAY_STUCK_OPEN_FAULT
堆内主正继电器粘连告警汇总 Summary of main positive contactor stuck close alarm at each string | 54 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CTSC_MAIN_POSITIVE_RELAY_STUCK_CLOSE_FAULT | RBMS_CTSC_MAIN_POSITIVE_RELAY_STUCK_CLOSE_FAULT
堆内主负继电器粘连告警汇总 Summary of main negative contactor stuck close alarm at each string | 55 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CTSC_MAIN_NEGATIVE_RELAY_STUCK_CLOSE_FAULT | RBMS_CTSC_MAIN_NEGATIVE_RELAY_STUCK_CLOSE_FAULT
堆 BMS 轻度与中度告警汇总 Summary of BMS system slight and medium alarm | 56 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | FaultLv | BBMS_SumInfo_Data | (BBMS_BMSMaxFltLevel == 2) ¦¦ (BBMS_BMSMaxFltLevel == 3 ) | (BBMS_BMSMaxFltLevel == 2) ¦¦ (BBMS_BMSMaxFltLevel == 3 )
堆 BMS 重度告警汇总 Summary of BMS system serious alarm | 57 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | FaultLv | BBMS_SumInfo_Data | BBMS_BMSMaxFltLevel == 1 | BBMS_BMSMaxFltLevel == 1
预留 Reserved | 58-69 |  | 1 | 1 | 0
堆内各极柱过温轻度告警汇总 Summary of pole over temperature slight alarm at each string | 70 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLTH_POLE_OVER_TEMPERATURE_LEVEL3_FAULT | RBMS_CLTH_POLE_OVER_TEMPERATURE_LEVEL3_FAULT
堆内各极柱过温中度告警汇总 Summary of pole over temperature medium alarm at each string | 71 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLTH_POLE_OVER_TEMPERATURE_LEVEL2_FAULT | RBMS_CLTH_POLE_OVER_TEMPERATURE_LEVEL2_FAULT
堆内各极柱过温重度告警汇总 Summary of pole over temperature serious alarm at each string | 72 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLTH_POLE_OVER_TEMPERATURE_LEVEL1_FAULT | RBMS_CLTH_POLE_OVER_TEMPERATURE_LEVEL1_FAULT
堆内模块电压过压轻度告警汇总 Summary of pack overvoltage slight alarm at each string | 73 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLVH_MODULE_OVER_VOLTAGE_LEVEL3_FAULT | RBMS_CLVH_MODULE_OVER_VOLTAGE_LEVEL3_FAULT
堆内模块电压过压中度告警汇总 Summary of pack overvoltage medium alarm at each string | 74 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLVH_MODULE_OVER_VOLTAGE_LEVEL2_FAULT | RBMS_CLVH_MODULE_OVER_VOLTAGE_LEVEL2_FAULT
堆内模块电压过压重度告警汇总 Summary of pack overvoltage serious alarm at each string | 75 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLVH_MODULE_OVER_VOLTAGE_LEVEL1_FAULT | RBMS_CLVH_MODULE_OVER_VOLTAGE_LEVEL1_FAULT
堆内模块电压欠压轻度告警汇总 Summary of pack undervoltage slight alarm at each string | 76 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLVH_MODULE_UNDER_VOLTAGE_LEVEL3_FAULT | RBMS_CLVH_MODULE_UNDER_VOLTAGE_LEVEL3_FAULT
堆内模块电压欠压中度告警汇总 Summary of pack undervoltage medium alarm at each string | 77 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLVH_MODULE_UNDER_VOLTAGE_LEVEL2_FAULT | RBMS_CLVH_MODULE_UNDER_VOLTAGE_LEVEL2_FAULT
堆内模块电压欠压重度告警汇总 Summary of pack undervoltage serious alarm at each string | 78 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_CLVH_MODULE_UNDER_VOLTAGE_LEVEL1_FAULT | RBMS_CLVH_MODULE_UNDER_VOLTAGE_LEVEL1_FAULT
堆内电压采集失联告警汇总 Summary of cell voltage acquisition alarm at each string | 79 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_AFES_AFE_FAULT ¦¦ RBMS_AFES_CELL_VOLTAGE_SAMPLING_LINE_OFF_FAULT | RBMS_AFES_AFE_FAULT ¦¦ RBMS_AFES_CELL_VOLTAGE_SAMPLING_LINE_OFF_FAULT
堆内温度采集失联告警汇总 Summary of cell temperature acquisition alarm at each string | 80 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | RBMS_Fault_Data | RBMS_AFES_AFE_FAULT ¦¦ RBMS_CLTS_CELL_TEMPERATURE_SAMPLING_MUX_FAULT | RBMS_AFES_AFE_FAULT ¦¦ RBMS_CLTS_CELL_TEMPERATURE_SAMPLING_MUX_FAULT
堆总控与EMS通讯丢失告警 EMS to BMS communication lost alarm | 81 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_EMCR_EMS_TO_BMS_COMMUNICATION_LOST_FAULT | BBMS_EMCR_EMS_TO_BMS_COMMUNICATION_LOST_FAULT
堆总控与PCS通讯丢失告警 PCS to BMS communication lost alarm | 82 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_EMCR_PCS_TO_BANK_COMMUNICATION_LOST_FAULT | BBMS_EMCR_PCS_TO_BANK_COMMUNICATION_LOST_FAULT
堆总控与TMS通讯丢失告警 TMS to BMS communication lost alarm | 83 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_TMCR_TMS_TO_BANK_COMMUNICATION_LOST_FAULT
堆总控与UPS通讯丢失告警 UPS to BMS communication lost alarm | 84 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_EMCR_UPS_TO_BMS_COMMUNICATION_LOST_FAULT | BBMS_EMCR_UPS_TO_BMS_COMMUNICATION_LOST_FAULT
堆总控与电表通讯丢失告警 Energymeter to BMS communication lost alarm | 85 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_EMCR_ENERGYMETER_TO_BMS_COMMUNICATION_LOST_FAULT | BBMS_EMCR_ENERGYMETER_TO_BMS_COMMUNICATION_LOST_FAULT
备电SPD1告警 Bakeup power spd alarm | 86 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_ACIS_BAKEUP_POWER_SPD_FAULT
可燃气体告警告警 Conbustile gas alarm | 87 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_ACIS_CONBUSTILE_GAS_FAULT
集装箱急停告警 Container EPO alarm | 88 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_ACIS_CONTAINER_EPO_FAULT
配电柜急停告警 Distribution cab epo alarm | 89 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_ACIS_DISTRIBUTION_CAB_EPO_FAULT
门禁告警 Door open alarm | 90 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_ACIS_DOOR_OPEN_FAULT
急停告警 Estop alarm | 91 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_ACIS_ESTOP_FAULT
防爆风机告警告警 Explosion proof fan alarm | 92 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_ACIS_EXPLOSIONPROOF_FAN_FAULT
客户外部急停告警 External EPO alarm | 93 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_ACIS_EXTERNAL_EPO_FAULT
消防火警启动异常 Fire alarm activated alarm | 94 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_ACIS_FIRE_ALARM_ACTIVATED_FAULT
消防二级告警 Fire extinguisher alarm alarm | 95 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_ACIS_FIRE_EXTINGUISHER_ALARM_FAULT
消防一级告警 Fire extinguisher alert alarm | 96 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_ACIS_FIRE_EXTINGUISHER_ALERT_FAULT
消防告警 Fire extinguisher warn alarm | 97 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_ACIS_FIRE_EXTINGUISHER_WARN_FAULT
IDLearm编码失败告警 IDLearm failed alarm | 98 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_ACIS_IDLEARN_FAILED_FAULT
PCS急停告警 PCS EPO alarm | 99 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_ACIS_PCS_EPO_FAULT | BBMS_ACIS_PCS_EPO_FAULT
QF1断路器告警 QF1 breaker alarm | 100 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_ACIS_QF1_BREAKER_FAULT
中控柜直流SPD浪涌告警 SPD dc surge alarm | 101 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_ACIS_SPD_DC_SURGE_FAULT
SPD2浪涌告警 SPD2 surge alarm | 102 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_ACIS_SPD2_SURGE_FAULT
水浸告警告警 Water flood alarm | 103 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_ACIS_WATER_FLOOD_FAULT
簇间环流越限轻度告警 String differential current slight alarm | 104 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_BKPC_DELTA_BRANCH_OVERCURRENT_LEVEL3_FAULT | BBMS_BKPC_DELTA_BRANCH_OVERCURRENT_LEVEL3_FAULT
簇间环流越限中度告警 String differential current medium alarm | 105 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_BKPC_DELTA_BRANCH_OVERCURRENT_LEVEL2_FAULT | BBMS_BKPC_DELTA_BRANCH_OVERCURRENT_LEVEL2_FAULT
簇间环流越限重度告警 String differential current serious alarm | 106 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_BKPC_DELTA_BRANCH_OVERCURRENT_LEVEL1_FAULT | BBMS_BKPC_DELTA_BRANCH_OVERCURRENT_LEVEL1_FAULT
簇间温差过大告警 String differential temperature alarm | 107 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_BKPC_DELTA_BRANCH_OVERTEMP_FAULT | BBMS_BKPC_DELTA_BRANCH_OVERTEMP_FAULT
过功率告警 Overpower alarm | 108 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_BSOX_OVERPOWER_FAULT | BBMS_BSOX_OVERPOWER_FAULT
簇间SOC差距过大告警 String differential SOC alarm | 109 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_BSOX_SOC_DIFF_FAULT | BBMS_BSOX_SOC_DIFF_FAULT
A核通讯告警 ACore communication alarm | 110 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_EMCR_A_CORE_COMMUNICATION_FAULT | BBMS_EMCR_A_CORE_COMMUNICATION_FAULT
所有簇CAN通讯丢失告警 All rack to bank CAN communication lost alarm | 111 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_EMCR_ALLRACK_TO_BANK_CAN_COMMUNICATION_LOST_FAULT | BBMS_EMCR_ALLRACK_TO_BANK_CAN_COMMUNICATION_LOST_FAULT
所有簇通讯丢失告警 All rack to bank communication lost alarm | 112 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_EMCR_ALLRACK_TO_BANK_COMMUNICATION_LOST_FAULT | BBMS_EMCR_ALLRACK_TO_BANK_COMMUNICATION_LOST_FAULT
电池舱除湿机通讯节点丢失告警 Battery Cabin Dehumidifier to BMS communication lost alarm | 113 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_EMCR_BATTERYCABIN_DEHUMIDIFIER_TO_BMS_COMM_LOST_FAULT
至少一个簇的CAN通讯丢失告警 One rack to bank CAN communication lost alarm | 114 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_EMCR_ONERACK_TO_BANK_CAN_COMMUNICATION_LOST_FAULT | BBMS_EMCR_ONERACK_TO_BANK_CAN_COMMUNICATION_LOST_FAULT
市电异常重度告警 Power supply abnormal serious alarm | 115 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_EMCR_POWER_SUPPLY_ABNORMAL_LEVEL1_FAULT | BBMS_EMCR_POWER_SUPPLY_ABNORMAL_LEVEL1_FAULT
12V电压超范围告警 12V internal power supply overorunder voltage alarm | 116 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_LVPS_12V_INTERNAL_POWER_SUPPLY_OVERORUNDER_VOLTAGE_FAULT | BBMS_LVPS_12V_INTERNAL_POWER_SUPPLY_OVERORUNDER_VOLTAGE_FAULT
24V电压超范围告警 24V internal power supply overorunder voltage alarm | 117 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_LVPS_24V_INTERNAL_POWER_SUPPLY_OVERORUNDER_VOLTAGE_FAULT | BBMS_LVPS_24V_INTERNAL_POWER_SUPPLY_OVERORUNDER_VOLTAGE_FAULT
水冷机轻度告警 TMS slight alarm | 118 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_THMC_TMS_LEVEL3_FAULT
水冷机中度告警 TMS medium alarm | 119 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_THMC_TMS_LEVEL2_FAULT
水冷机重度告警 TMS serious alarm | 120 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_THMC_TMS_LEVEL1_FAULT
水冷机组工作模式不匹配告警 TMS request and work mode different alarm | 121 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_THMC_TMS_REQUEST_DIFF_FAULT
市电异常轻度告警 Power supply abnormal slight alarm | 122 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Bank | Fault | BBMS_Fault_Data | BBMS_EMCR_POWER_SUPPLY_ABNORMAL_LEVEL3_FAULT
预留 Reserved | 123-199 |  | 1 | 1 | 0
簇 (i+1) 主控与总控通讯失联 String (i+1) ESBCM Lost communication | i * 200 + 200 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_EMCR_RANK_TO_BANK_COMMUNICATION_LOST_FAULT | RBMS_EMCR_RANK_TO_BANK_COMMUNICATION_LOST_FAULT
簇 (i+1) 端电压欠压轻度告警 String (i+1) Total voltage undervoltage slight alarm | i * 200 + 201 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_HVSH_BATTERY_UNDER_VOLTAGE_LEVEL3_FAULT | RBMS_HVSH_BATTERY_UNDER_VOLTAGE_LEVEL3_FAULT
簇 (i+1) 端电压欠压中度告警 String (i+1) Total voltage undervoltage medium alarm | i * 200 + 202 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_HVSH_BATTERY_UNDER_VOLTAGE_LEVEL2_FAULT | RBMS_HVSH_BATTERY_UNDER_VOLTAGE_LEVEL2_FAULT
簇 (i+1) 端电压欠压重度告警 String (i+1) Total voltage undervoltage serious alarm | i * 200 + 203 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_HVSH_BATTERY_UNDER_VOLTAGE_LEVEL1_FAULT | RBMS_HVSH_BATTERY_UNDER_VOLTAGE_LEVEL1_FAULT
簇 (i+1) 端电压过压轻度告警 String (i+1) Total voltage overvoltage slight alarm | i * 200 + 204 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_HVSH_BATTERY_OVER_VOLTAGE_LEVEL3_FAULT | RBMS_HVSH_BATTERY_OVER_VOLTAGE_LEVEL3_FAULT
簇 (i+1) 端电压过压中度告警 String (i+1) Total voltage overvoltage medium alarm | i * 200 + 205 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_HVSH_BATTERY_OVER_VOLTAGE_LEVEL2_FAULT | RBMS_HVSH_BATTERY_OVER_VOLTAGE_LEVEL2_FAULT
簇 (i+1) 端电压过压重度告警 String (i+1) Total voltage overvoltage serious alarm | i * 200 + 206 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_HVSH_BATTERY_OVER_VOLTAGE_LEVEL1_FAULT | RBMS_HVSH_BATTERY_OVER_VOLTAGE_LEVEL1_FAULT
簇 (i+1) 端充电电流轻度告警 String (i+1) charge overcurrent slight alarm | i * 200 + 207 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_BTCD_RECHARGE_OVER_CURRENT_LEVEL3_FAULT | RBMS_BTCD_RECHARGE_OVER_CURRENT_LEVEL3_FAULT
簇 (i+1) 端充电电流中度告警 String (i+1) charge overcurrent medium alarm | i * 200 + 208 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_BTCD_RECHARGE_OVER_CURRENT_LEVEL2_FAULT | RBMS_BTCD_RECHARGE_OVER_CURRENT_LEVEL2_FAULT
簇 (i+1) 端充电电流重度告警 String (i+1) charge overcurrent serious alarm | i * 200 + 209 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_BTCD_RECHARGE_OVER_CURRENT_LEVEL1_FAULT | RBMS_BTCD_RECHARGE_OVER_CURRENT_LEVEL1_FAULT
簇 (i+1) 端放电电流轻度告警 String (i+1) discharge overcurrent slight alarm | i * 200 + 210 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_BTCD_DISCHARGE_OVER_CURRENT_LEVEL3_FAULT | RBMS_BTCD_DISCHARGE_OVER_CURRENT_LEVEL3_FAULT
簇 (i+1) 端放电电流中度告警 String (i+1) discharge overcurrent medium alarm | i * 200 + 211 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_BTCD_DISCHARGE_OVER_CURRENT_LEVEL2_FAULT | RBMS_BTCD_DISCHARGE_OVER_CURRENT_LEVEL2_FAULT
簇 (i+1) 端放电电流重度告警 String (i+1) discharge overcurrent serious alarm | i * 200 + 212 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_BTCD_DISCHARGE_OVER_CURRENT_LEVEL1_FAULT | RBMS_BTCD_DISCHARGE_OVER_CURRENT_LEVEL1_FAULT
簇 (i+1) 单体欠压轻度告警 String (i+1) cell voltage undervoltage slight alarm | i * 200 + 213 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_MINCELLV_UV_LEVEL3_FAULT | RBMS_CLVH_MINCELLV_UV_LEVEL3_FAULT
簇 (i+1) 单体欠压中度告警 String (i+1) cell voltage undervoltage medium alarm | i * 200 + 214 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_MINCELLV_UV_LEVEL2_FAULT | RBMS_CLVH_MINCELLV_UV_LEVEL2_FAULT
簇 (i+1) 单体欠压重度告警 String (i+1) cell voltage undervoltage serious alarm | i * 200 + 215 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_MINCELLV_UV_LEVEL1_FAULT | RBMS_CLVH_MINCELLV_UV_LEVEL1_FAULT
簇 (i+1) 单体过压轻度告警 String (i+1) cell voltage overvoltage slight alarm | i * 200 + 216 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_MAXCELLV_OV_LEVEL3_FAULT | RBMS_CLVH_MAXCELLV_OV_LEVEL3_FAULT
簇 (i+1) 单体过压中度告警 String (i+1) cell voltage overvoltage medium alarm | i * 200 + 217 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_MAXCELLV_OV_LEVEL2_FAULT | RBMS_CLVH_MAXCELLV_OV_LEVEL2_FAULT
簇 (i+1) 单体过压重度告警 String (i+1) cell voltage overvoltage serious alarm | i * 200 + 218 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_MAXCELLV_OV_LEVEL1_FAULT | RBMS_CLVH_MAXCELLV_OV_LEVEL1_FAULT
簇 (i+1) 单体充电欠温轻度告警 String (i+1) cell charge low temperature slight alarm | i * 200 + 219 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_CHG_UNDER_TEMPERATURE_LEVEL3_FAULT | RBMS_CLTH_CHG_UNDER_TEMPERATURE_LEVEL3_FAULT
簇 (i+1) 单体充电欠温中度告警 String (i+1) cell charge low temperature medium alarm | i * 200 + 220 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_CHG_UNDER_TEMPERATURE_LEVEL2_FAULT | RBMS_CLTH_CHG_UNDER_TEMPERATURE_LEVEL2_FAULT
簇 (i+1) 单体充电欠温重度告警 String (i+1) cell charge low temperature serious alarm | i * 200 + 221 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_CHG_UNDER_TEMPERATURE_LEVEL1_FAULT | RBMS_CLTH_CHG_UNDER_TEMPERATURE_LEVEL1_FAULT
簇 (i+1) 单体充电过温轻度告警 String (i+1) cell charge over temperature slight alarm | i * 200 + 222 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_CHG_OVER_TEMPERATURE_LEVEL3_FAULT | RBMS_CLTH_CHG_OVER_TEMPERATURE_LEVEL3_FAULT
簇 (i+1) 单体充电过温中度告警 String (i+1) cell charge over temperature medium alarm | i * 200 + 223 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_CHG_OVER_TEMPERATURE_LEVEL2_FAULT | RBMS_CLTH_CHG_OVER_TEMPERATURE_LEVEL2_FAULT
簇 (i+1) 单体充电过温重度告警 String (i+1) cell charge over temperature serious alarm | i * 200 + 224 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_CHG_OVER_TEMPERATURE_LEVEL1_FAULT | RBMS_CLTH_CHG_OVER_TEMPERATURE_LEVEL1_FAULT
簇 (i+1) 单体放电欠温轻度告警 String (i+1) cell discharge low temperature slight alarm | i * 200 + 225 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_DSG_UNDER_TEMPERATURE_LEVEL3_FAULT | RBMS_CLTH_DSG_UNDER_TEMPERATURE_LEVEL3_FAULT
簇 (i+1) 单体放电欠温中度告警 String (i+1) cell discharge low temperature medium alarm | i * 200 + 226 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_DSG_UNDER_TEMPERATURE_LEVEL2_FAULT | RBMS_CLTH_DSG_UNDER_TEMPERATURE_LEVEL2_FAULT
簇 (i+1) 单体放电欠温重度告警 String (i+1) cell discharge low temperature serious alarm | i * 200 + 227 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_DSG_UNDER_TEMPERATURE_LEVEL1_FAULT | RBMS_CLTH_DSG_UNDER_TEMPERATURE_LEVEL1_FAULT
簇 (i+1) 单体放电过温轻度告警 String (i+1) cell discharge over temperature slight alarm | i * 200 + 228 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_DSG_OVER_TEMPERATURE_LEVEL3_FAULT | RBMS_CLTH_DSG_OVER_TEMPERATURE_LEVEL3_FAULT
簇 (i+1) 单体放电过温中度告警 String (i+1) cell discharge over temperature medium alarm | i * 200 + 229 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_DSG_OVER_TEMPERATURE_LEVEL2_FAULT | RBMS_CLTH_DSG_OVER_TEMPERATURE_LEVEL2_FAULT
簇 (i+1) 单体放电过温重度告警 String (i+1) cell discharge over temperature serious alarm | i * 200 + 230 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_DSG_OVER_TEMPERATURE_LEVEL1_FAULT | RBMS_CLTH_DSG_OVER_TEMPERATURE_LEVEL1_FAULT
簇 (i+1) 单体 SOC 低轻度告警 String (i+1) cell SOC low slight alarm | i * 200 + 231 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_SOCA_SOC_TOO_LOW_LEVEL3_FAULT | RBMS_SOCA_SOC_TOO_LOW_LEVEL3_FAULT
簇 (i+1) 单体 SOC 低中度告警 String (i+1) cell SOC low medium alarm | i * 200 + 232 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_SOCA_SOC_TOO_LOW_LEVEL2_FAULT | RBMS_SOCA_SOC_TOO_LOW_LEVEL2_FAULT
簇 (i+1) 单体 SOC 低重度告警 String (i+1) cell SOC low serious alarm | i * 200 + 233 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_SOCA_SOC_TOO_LOW_LEVEL1_FAULT | RBMS_SOCA_SOC_TOO_LOW_LEVEL1_FAULT
簇 (i+1) 单体 SOC 高轻度告警 String (i+1) cell SOC high slight alarm | i * 200 + 234 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_SOCA_SOC_TOO_HIGH_LEVEL3_FAULT | RBMS_SOCA_SOC_TOO_HIGH_LEVEL3_FAULT
簇 (i+1) 单体 SOC 高中度告警 String (i+1) cell SOC high medium alarm | i * 200 + 235 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_SOCA_SOC_TOO_HIGH_LEVEL2_FAULT | RBMS_SOCA_SOC_TOO_HIGH_LEVEL2_FAULT
簇 (i+1) 单体 SOC 高重度告警 String (i+1) cell SOC high serious alarm | i * 200 + 236 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_SOCA_SOC_TOO_HIGH_LEVEL1_FAULT | RBMS_SOCA_SOC_TOO_HIGH_LEVEL1_FAULT
簇 (i+1) 单体 SOH 低轻度告警 String (i+1) cell SOH low slight alarm | i * 200 + 237 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_SOHA_SOH_TOO_LOW_LEVEL3_FAULT | RBMS_SOHA_SOH_TOO_LOW_LEVEL3_FAULT
簇 (i+1) 单体 SOH 低中度告警 String (i+1) cell SOH low medium alarm | i * 200 + 238 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_SOHA_SOH_TOO_LOW_LEVEL2_FAULT | RBMS_SOHA_SOH_TOO_LOW_LEVEL2_FAULT
簇 (i+1) 单体 SOH 低重度告警 String (i+1) cell SOH low serious alarm | i * 200 + 239 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_SOHA_SOH_TOO_LOW_LEVEL1_FAULT | RBMS_SOHA_SOH_TOO_LOW_LEVEL1_FAULT
簇 (i+1) 单体压差轻度告警 String (i+1) cell voltage different slight alarm | i * 200 + 240 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_DELTACELLV_OL_LEVEL3_FAULT | RBMS_CLVH_DELTACELLV_OL_LEVEL3_FAULT
簇 (i+1) 单体压差中度告警 String (i+1) cell voltage different medium alarm | i * 200 + 241 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_DELTACELLV_OL_LEVEL2_FAULT | RBMS_CLVH_DELTACELLV_OL_LEVEL2_FAULT
簇 (i+1) 单体压差重度告警 String (i+1) cell voltage different serious alarm | i * 200 + 242 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_DELTACELLV_OL_LEVEL1_FAULT | RBMS_CLVH_DELTACELLV_OL_LEVEL1_FAULT
簇 (i+1) 单体温差轻度告警 String (i+1) cell temperature different slight alarm | i * 200 + 243 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_DELTA_TEMPERATURE_TOO_MUCH_LEVEL3_FAULT | RBMS_CLTH_DELTA_TEMPERATURE_TOO_MUCH_LEVEL3_FAULT
簇 (i+1) 单体温差中度告警 String (i+1) cell temperature different medium alarm | i * 200 + 244 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_DELTA_TEMPERATURE_TOO_MUCH_LEVEL2_FAULT | RBMS_CLTH_DELTA_TEMPERATURE_TOO_MUCH_LEVEL2_FAULT
簇 (i+1) 单体温差重度告警 String (i+1) cell temperature different serious alarm | i * 200 + 245 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_DELTA_TEMPERATURE_TOO_MUCH_LEVEL1_FAULT | RBMS_CLTH_DELTA_TEMPERATURE_TOO_MUCH_LEVEL1_FAULT
簇 (i+1) 放电极限过流告警 String (i+1) discharge overcurrent limit alarm | i * 200 + 246 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_BTCD_DISCHARGE_OVER_CURRENT_LEVEL0_FAULT | RBMS_BTCD_DISCHARGE_OVER_CURRENT_LEVEL0_FAULT
簇 (i+1) 充电极限过流告警 String (i+1) charge overcurrent limit alarm | i * 200 + 247 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_BTCD_RECHARGE_OVER_CURRENT_LEVEL0_FAULT | RBMS_BTCD_RECHARGE_OVER_CURRENT_LEVEL0_FAULT
簇 (i+1) 电流传感器零漂告警 String (i+1) current sensor zero drift alarm | i * 200 + 248 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_BTCS_CANBATI_ZERODRIFT_FAULT | RBMS_BTCS_CANBATI_ZERODRIFT_FAULT
簇 (i+1) 均衡回路告警 String (i+1) balancing circuit alarm | i * 200 + 249 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CBSS_BALANCING_LOOP_CIRCUIT_FAULT | RBMS_CBSS_BALANCING_LOOP_CIRCUIT_FAULT
簇 (i+1) AFE芯片过温告警 String (i+1) AFE chip overtemperature alarm | i * 200 + 250 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_AFES_AFE_OVER_TEMPERATURE_FAULT | RBMS_AFES_AFE_OVER_TEMPERATURE_FAULT
簇 (i+1) 电芯电压冗余检测告警 String (i+1) cell voltage redundancy detection alarm | i * 200 + 251 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_AFES_CELL_VOLTAGE_REDUNDABCY_DETECT_FAULT | RBMS_AFES_CELL_VOLTAGE_REDUNDABCY_DETECT_FAULT
簇 (i+1) 菊花链通信Counter告警 String (i+1) daisy-chain communication counter alarm | i * 200 + 252 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_AFES_DAISY_CHAIN_COUNTER_ERROR_FAULT | RBMS_AFES_DAISY_CHAIN_COUNTER_ERROR_FAULT
簇 (i+1) 菊花链多点断线告警 String (i+1) daisy-chain multi-point disconnection alarm | i * 200 + 253 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_AFES_DAISY_CHAIN_MULTIPLE_POINT_OFF_FAULT | RBMS_AFES_DAISY_CHAIN_MULTIPLE_POINT_OFF_FAULT
簇 (i+1) 菊花链单点断线告警 String (i+1) daisy-chain single-point disconnection alarm | i * 200 + 254 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_AFES_DAISY_CHAIN_SINGLE_POINT_OFF_FAULT | RBMS_AFES_DAISY_CHAIN_SINGLE_POINT_OFF_FAULT
簇 (i+1) NTC供电告警 String (i+1) NTC power supply alarm | i * 200 + 255 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_AFES_NTC_POWER_SUPPLY_FAULT | RBMS_AFES_NTC_POWER_SUPPLY_FAULT
簇 (i+1) AFE硬件告警 String (i+1) AFE hardware fault | i * 200 + 256 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_AFES_AFE_FAULT | RBMS_AFES_AFE_FAULT
簇 (i+1) 菊花链通信丢失告警 String (i+1) daisy chain communication lost fault | i * 200 + 257 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_AFES_DAISY_CHAIN_NO_UPDATE_FAULT | RBMS_AFES_DAISY_CHAIN_NO_UPDATE_FAULT
簇 (i+1) 电芯电压温度采样CRC告警 String (i+1) cell voltage and temperature sampling CRC fault | i * 200 + 258 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_AFES_CRC_FAULT | RBMS_AFES_CRC_FAULT
簇 (i+1) 电芯电压采样线掉线 String (i+1) cell voltage sampling line disconnected | i * 200 + 259 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_AFES_CELL_VOLTAGE_SAMPLING_LINE_OFF_FAULT | RBMS_AFES_CELL_VOLTAGE_SAMPLING_LINE_OFF_FAULT
簇 (i+1) 电芯温度采样短地(STG) String (i+1) cell temperature sampling short to ground (STG) | i * 200 + 260 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTS_CELL_TEMPERATURE_OUT_OF_RANGE_HIGH_FAULT | RBMS_CLTS_CELL_TEMPERATURE_OUT_OF_RANGE_HIGH_FAULT
簇 (i+1) 电芯温度采样短电源(STB or Oc) String (i+1) cell temperature sampling short to power supply (STB or Oc) | i * 200 + 261 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTS_CELL_TEMPERATURE_OUT_OF_RANGE_LOW_FAULT | RBMS_CLTS_CELL_TEMPERATURE_OUT_OF_RANGE_LOW_FAULT
簇 (i+1) 电芯温度采样MUX告警 String (i+1) cell temperature sampling MUX fault | i * 200 + 262 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTS_CELL_TEMPERATURE_SAMPLING_MUX_FAULT | RBMS_CLTS_CELL_TEMPERATURE_SAMPLING_MUX_FAULT
簇 (i+1) 电芯电压采样超范围 String (i+1) cell voltage sampling out of range | i * 200 + 263 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVS_CELL_VOLTAGE_OUT_OF_RANGE_FAULT | RBMS_CLVS_CELL_VOLTAGE_OUT_OF_RANGE_FAULT
簇 (i+1) 高压采样传感器告警 String (i+1) high-voltage sampling sensor fault | i * 200 + 264 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_HVSS_HIGH_VOLTAGE_SENSOR_FAULT | RBMS_HVSS_HIGH_VOLTAGE_SENSOR_FAULT
簇 (i+1) Battery电压超范围告警 String (i+1) battery voltage out of range fault | i * 200 + 265 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_HVSS_BATTERY_VOLTAGE_OUT_OF_RANGE_FAULT | RBMS_HVSS_BATTERY_VOLTAGE_OUT_OF_RANGE_FAULT
簇 (i+1) LinkPos电压超范围告警 String (i+1) LinkPos voltage out of range fault | i * 200 + 266 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_HVSS_LINK_POSITIVE_VOLTAGE_OUT_OF_RANGE_FAULT | RBMS_HVSS_LINK_POSITIVE_VOLTAGE_OUT_OF_RANGE_FAULT
簇 (i+1) 电流传感器通讯丢失告警 String (i+1) current sensor communication lost fault | i * 200 + 267 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_BTCS_CANMSG_TIMEOUT_FAULT | RBMS_BTCS_CANMSG_TIMEOUT_FAULT
簇 (i+1) 电流传感器硬件告警 String (i+1) current sensor hardware fault | i * 200 + 268 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_BTCS_CANBATI_IMPLY_FAULT | RBMS_BTCS_CANBATI_IMPLY_FAULT
簇 (i+1) 电流传感器CRC告警 String (i+1) current sensor CRC fault | i * 200 + 269 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_BTCS_CANMSG_CRCRES_FAULT | RBMS_BTCS_CANMSG_CRCRES_FAULT
簇 (i+1) 预留 String (i+1) Reserved | i * 200 + 270 |  | 1 | 1 | 0
簇 (i+1) 单体极限过压 String (i+1) single cell extreme overvoltage | i * 200 + 271 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_MAXCELLV_OV_LEVEL4_FAULT | RBMS_CLVH_MAXCELLV_OV_LEVEL4_FAULT
簇 (i+1) 单体极限欠压 String (i+1) single cell extreme undervoltage | i * 200 + 272 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_MINCELLV_UV_LEVEL4_FAULT | RBMS_CLVH_MINCELLV_UV_LEVEL4_FAULT
簇 (i+1) 高压回路断路告警 String (i+1) high-voltage circuit open fault | i * 200 + 273 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_HVSH_HIGH_VOLTAGE_LOOP_BROKEN_FAULT | RBMS_HVSH_HIGH_VOLTAGE_LOOP_BROKEN_FAULT
簇 (i+1) 电芯极限过温 String (i+1) cell extreme overtemperature | i * 200 + 274 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_OVER_TEMPERATURE_LEVEL0_FAULT | RBMS_CLTH_OVER_TEMPERATURE_LEVEL0_FAULT
簇 (i+1) 电芯温升过快 String (i+1) cell temperature rising too fast | i * 200 + 275 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_TEMPERATURE_RISE_TOO_FAST_FAULT | RBMS_CLTH_TEMPERATURE_RISE_TOO_FAST_FAULT
簇 (i+1) 电芯热失控 String (i+1) cell thermal runaway | i * 200 + 276 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_THERMAL_RUNAWAY_FAULT | RBMS_CLTH_THERMAL_RUNAWAY_FAULT
簇 (i+1) 从板均衡温度高重度告警 String (i+1) slave board balancing temperature serious alarm | i * 200 + 277 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_PCB_BOARD_OVER_TEMPERATURE1_FAULT | RBMS_CLTH_PCB_BOARD_OVER_TEMPERATURE1_FAULT
簇 (i+1) 高压绝缘低重度告警 String (i+1) high-voltage insulation serious alarm | i * 200 + 278 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_ISOH_ISOLATION_LOW_LEVEL1_FAULT | RBMS_ISOH_ISOLATION_LOW_LEVEL1_FAULT
簇 (i+1) 绝缘无效告警 String (i+1) insulation invalid fault | i * 200 + 279 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_ISOH_ISOLATION_VALUE_INVALID_FAULT | RBMS_ISOH_ISOLATION_VALUE_INVALID_FAULT
簇 (i+1) 电芯自放电差异过重度告警 String (i+1) cell self-discharge difference serious alarm | i * 200 + 280 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CBCC_SELF_DISCHARGE_DIFFERENCE_OVER_HIGH1_FAULT | RBMS_CBCC_SELF_DISCHARGE_DIFFERENCE_OVER_HIGH1_FAULT
簇 (i+1) 过充告警 String (i+1) overcharge alarm | i * 200 + 281 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_SOCA_RACK_OVER_CHARGE_FAULT | RBMS_SOCA_RACK_OVER_CHARGE_FAULT
簇 (i+1) 主负继电器粘连告警 String (i+1) main negative relay stuck close alarm | i * 200 + 282 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CTSC_MAIN_NEGATIVE_RELAY_STUCK_CLOSE_FAULT | RBMS_CTSC_MAIN_NEGATIVE_RELAY_STUCK_CLOSE_FAULT
簇 (i+1) 主负继电器开路告警 String (i+1) main negative relay open circuit alarm | i * 200 + 283 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CTSC_MAIN_NEGATIVE_RELAY_STUCK_OPEN_FAULT | RBMS_CTSC_MAIN_NEGATIVE_RELAY_STUCK_OPEN_FAULT
簇 (i+1) 主正继电器粘连告警 String (i+1) main positive relay stuck close alarm | i * 200 + 284 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CTSC_MAIN_POSITIVE_RELAY_STUCK_CLOSE_FAULT | RBMS_CTSC_MAIN_POSITIVE_RELAY_STUCK_CLOSE_FAULT
簇 (i+1) 主正继电器开路告警 String (i+1) main positive relay open circuit alarm | i * 200 + 285 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CTSC_MAIN_POSITIVE_RELAY_STUCK_OPEN_FAULT | RBMS_CTSC_MAIN_POSITIVE_RELAY_STUCK_OPEN_FAULT
簇 (i+1) 极柱温度过高轻度告警 String (i+1) pole temperature high slight alarm | i * 200 + 286 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_POLE_OVER_TEMPERATURE_LEVEL3_FAULT | RBMS_CLTH_POLE_OVER_TEMPERATURE_LEVEL3_FAULT
簇 (i+1) 极柱温度过高中度告警 String (i+1) pole temperature high medium alarm | i * 200 + 287 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_POLE_OVER_TEMPERATURE_LEVEL2_FAULT | RBMS_CLTH_POLE_OVER_TEMPERATURE_LEVEL2_FAULT
簇 (i+1) 极柱温度过高重度告警 String (i+1) pole temperature high serious alarm | i * 200 + 288 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_POLE_OVER_TEMPERATURE_LEVEL1_FAULT | RBMS_CLTH_POLE_OVER_TEMPERATURE_LEVEL1_FAULT
簇 (i+1) 模块电压过高轻度告警 String (i+1) pack voltage overvoltage slight alarm | i * 200 + 289 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_MODULE_OVER_VOLTAGE_LEVEL3_FAULT | RBMS_CLVH_MODULE_OVER_VOLTAGE_LEVEL3_FAULT
簇 (i+1) 模块电压过高中度告警 String (i+1) pack voltage overvoltage medium alarm | i * 200 + 290 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_MODULE_OVER_VOLTAGE_LEVEL2_FAULT | RBMS_CLVH_MODULE_OVER_VOLTAGE_LEVEL2_FAULT
簇 (i+1) 模块电压过高重度告警 String (i+1) pack voltage overvoltage serious alarm | i * 200 + 291 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_MODULE_OVER_VOLTAGE_LEVEL1_FAULT | RBMS_CLVH_MODULE_OVER_VOLTAGE_LEVEL1_FAULT
簇 (i+1) 模块电压过低轻度告警 String (i+1) pack voltage undervoltage slight alarm | i * 200 + 292 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_MODULE_UNDER_VOLTAGE_LEVEL3_FAULT | RBMS_CLVH_MODULE_UNDER_VOLTAGE_LEVEL3_FAULT
簇 (i+1) 模块电压过低中度告警 String (i+1) pack voltage undervoltage slight alarm | i * 200 + 293 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_MODULE_UNDER_VOLTAGE_LEVEL2_FAULT | RBMS_CLVH_MODULE_UNDER_VOLTAGE_LEVEL2_FAULT
簇 (i+1) 模块电压过低重度告警 String (i+1) pack voltage undervoltage slight alarm | i * 200 + 294 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_MODULE_UNDER_VOLTAGE_LEVEL1_FAULT | RBMS_CLVH_MODULE_UNDER_VOLTAGE_LEVEL1_FAULT
簇 (i+1) 预充超时告警 String (i+1) precharge timeout fault | i * 200 + 295 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CTSC_PRECHARGE_OVER_TIME_FAULT | RBMS_CTSC_PRECHARGE_OVER_TIME_FAULT
簇 (i+1) 预充过流告警 String (i+1) precharge overcurrent fault | i * 200 + 296 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CTSC_PRECHARGE_OVER_CURRENT_FAULT | RBMS_CTSC_PRECHARGE_OVER_CURRENT_FAULT
簇 (i+1) 消防重度告警 String (i+1) fire alarm serious alarm | i * 200 + 297 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_ACIS_FIRE_EXTINGUISHER_ALERT_FAULT | RBMS_ACIS_FIRE_EXTINGUISHER_ALERT_FAULT
簇 (i+1) 高压箱熔断器告警 String (i+1) high-voltage fuse alarm | i * 200 + 298 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_ACIS_HV_FUSE_FAULT | RBMS_ACIS_HV_FUSE_FAULT
簇 (i+1) MSD开路(互锁)告警 String (i+1) MSD open (interlock) alarm | i * 200 + 299 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_ACIS_MSD_OPEN_FAULT | RBMS_ACIS_MSD_OPEN_FAULT
簇 (i+1) 门禁告警 String (i+1) door open alarm | i * 200 + 300 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_ACIS_RBMS_DOOR_OPEN_FAULT | RBMS_ACIS_RBMS_DOOR_OPEN_FAULT
簇 (i+1) 隔离开关开告警 String (i+1) isolation switch open alarm | i * 200 + 301 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_ACIS_RBMS_QS_OPEN_FAULT | RBMS_ACIS_RBMS_QS_OPEN_FAULT
簇 (i+1) 主控SPD1浪涌反馈告警 String (i+1) main SPD1 surge feedback alarm | i * 200 + 302 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_ACIS_RBMS_SPD1_OPEN_FAULT | RBMS_ACIS_RBMS_SPD1_OPEN_FAULT
簇 (i+1) 电芯自放电差异过大轻度告警 String (i+1) cell self-discharge difference too large slight alarm | i * 200 + 303 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CBCC_SELF_DISCHARGE_DIFFERENCE_OVER_HIGH3_FAULT | RBMS_CBCC_SELF_DISCHARGE_DIFFERENCE_OVER_HIGH3_FAULT
簇 (i+1) 电芯自放电差异过大中度告警 String (i+1) cell self-discharge difference too large medium alarm | i * 200 + 304 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CBCC_SELF_DISCHARGE_DIFFERENCE_OVER_HIGH2_FAULT | RBMS_CBCC_SELF_DISCHARGE_DIFFERENCE_OVER_HIGH2_FAULT
簇 (i+1) 电芯单体温度与电芯极柱温度偏差过大重度告警 String (i+1) cell temperature vs post temperature deviation too large serious alarm | i * 200 + 305 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_CELL_POLE_DELTA_TEMPERATURE_OVER_LEVEL1_FAULT | RBMS_CLTH_CELL_POLE_DELTA_TEMPERATURE_OVER_LEVEL1_FAULT
簇 (i+1) 高压盒过温轻度告警 String (i+1) HV box overtemperature slight alarm | i * 200 + 306 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_HV_BOX_AMBIENT_OVER_TEMP_LEVEL3_FAULT | RBMS_CLTH_HV_BOX_AMBIENT_OVER_TEMP_LEVEL3_FAULT
簇 (i+1) 高压盒过温中度告警 String (i+1) HV box overtemperature medium alarm | i * 200 + 307 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_HV_BOX_AMBIENT_OVER_TEMP_LEVEL2_FAULT | RBMS_CLTH_HV_BOX_AMBIENT_OVER_TEMP_LEVEL2_FAULT
簇 (i+1) 高压盒过温重度告警 String (i+1) HV box overtemperature serious alarm | i * 200 + 308 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_HV_BOX_AMBIENT_OVER_TEMP_LEVEL1_FAULT | RBMS_CLTH_HV_BOX_AMBIENT_OVER_TEMP_LEVEL1_FAULT
簇 (i+1) Pack正负极连接件温度过温轻度告警 String (i+1) pack positive/negative connector overtemperature slight alarm | i * 200 + 309 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_PACKPOSNEGCONN_OVER_TEMPERATURE_LEVEL3_FAULT | RBMS_CLTH_PACKPOSNEGCONN_OVER_TEMPERATURE_LEVEL3_FAULT
簇 (i+1) Pack正负极连接件温度过温中度告警 String (i+1) pack positive/negative connector overtemperature medium alarm | i * 200 + 310 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_PACKPOSNEGCONN_OVER_TEMPERATURE_LEVEL2_FAULT | RBMS_CLTH_PACKPOSNEGCONN_OVER_TEMPERATURE_LEVEL2_FAULT
簇 (i+1) Pack正负极连接件温度过温重度告警 String (i+1) pack positive/negative connector overtemperature serious alarm | i * 200 + 311 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_PACKPOSNEGCONN_OVER_TEMPERATURE_LEVEL1_FAULT | RBMS_CLTH_PACKPOSNEGCONN_OVER_TEMPERATURE_LEVEL1_FAULT
簇 (i+1) 从板均衡温度高中度告警 String (i+1) slave board balancing temperature high medium alarm | i * 200 + 312 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_PCB_BOARD_OVER_TEMPERATURE2_FAULT | RBMS_CLTH_PCB_BOARD_OVER_TEMPERATURE2_FAULT
簇 (i+1) 电芯极限欠温告警 String (i+1) cell undervoltage limit alarm | i * 200 + 313 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTH_UNDER_TEMPERATURE_LEVEL0_FAULT | RBMS_CLTH_UNDER_TEMPERATURE_LEVEL0_FAULT
簇 (i+1) 电芯温度冗余检测告警 String (i+1) cell temperature redundancy detection alarm | i * 200 + 314 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTS_CELL_TEMPERATURE_REDUNDANT_DETECT_FAULT | RBMS_CLTS_CELL_TEMPERATURE_REDUNDANT_DETECT_FAULT
簇 (i+1) 从板均衡温度采样短电源(STB or Oc)告警 String (i+1) slave board balancing temperature sample short to power(STB or Oc) alarm | i * 200 + 315 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTS_PCB_BOARD_TEMP_SENSOR_SHORT_TO_BATTERY_FAULT | RBMS_CLTS_PCB_BOARD_TEMP_SENSOR_SHORT_TO_BATTERY_FAULT
簇 (i+1) 从板均衡温度采样短地(STG)告警 String (i+1) slave board balancing temperature sample short to ground(STG) alarm | i * 200 + 316 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLTS_PCB_BOARD_TEMP_SENSOR_SHORT_TO_GROUND_FAULT | RBMS_CLTS_PCB_BOARD_TEMP_SENSOR_SHORT_TO_GROUND_FAULT
簇 (i+1) 模组压差大轻度告警 String (i+1) module voltage difference too large slight alarm | i * 200 + 317 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_DELTAMODULEV_OL_LEVEL3_FAULT | RBMS_CLVH_DELTAMODULEV_OL_LEVEL3_FAULT
簇 (i+1) 模组压差大中度告警 String (i+1) module voltage difference too large medium alarm | i * 200 + 318 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_DELTAMODULEV_OL_LEVEL2_FAULT | RBMS_CLVH_DELTAMODULEV_OL_LEVEL2_FAULT
簇 (i+1) 模组压差大重度告警 String (i+1) module voltage difference too large serious alarm | i * 200 + 319 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_DELTAMODULEV_OL_LEVEL1_FAULT | RBMS_CLVH_DELTAMODULEV_OL_LEVEL1_FAULT
簇 (i+1) 单体电压和与AFE电压不匹配告警 String (i+1) cell voltage does not match AFE voltage alarm | i * 200 + 320 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVH_VOLTAGE_MISMATCH_FAULT | RBMS_CLVH_VOLTAGE_MISMATCH_FAULT
簇 (i+1) AFE电压采样超范围告警 String (i+1) AFE voltage sampling out of range alarm | i * 200 + 321 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CLVS_AFE_VOLTAGE_OUT_OF_RANGE_FAULT | RBMS_CLVS_AFE_VOLTAGE_OUT_OF_RANGE_FAULT
簇 (i+1) 主负继电器驱动电路告警 String (i+1) main negative relay drive circuit alarm | i * 200 + 322 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CTSC_MAIN_NEGATIVE_RELAY_DRIVER_CIRCUIT_FAULT | RBMS_CTSC_MAIN_NEGATIVE_RELAY_DRIVER_CIRCUIT_FAULT
簇 (i+1) 主正继电器驱动电路告警 String (i+1) main positive relay drive circuit alarm | i * 200 + 323 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CTSC_MAIN_POSITIVE_RELAY_DRIVER_CIRCUIT_FAULT | RBMS_CTSC_MAIN_POSITIVE_RELAY_DRIVER_CIRCUIT_FAULT
簇 (i+1) 继电器驱动回采选通告警 String (i+1) relay drive feedback gating alarm | i * 200 + 324 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_CTSC_RELAY_DRIVER_SAMPLING_SELECT_CHANNEL_FAULT | RBMS_CTSC_RELAY_DRIVER_SAMPLING_SELECT_CHANNEL_FAULT
簇 (i+1) Bank通信CRC异常告警 String (i+1) bank communication CRC abnormal alarm | i * 200 + 325 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_EMCR_CRC_FAULT | RBMS_EMCR_CRC_FAULT
簇 (i+1) 紧急关断信号CAN通信Counter告警 String (i+1) emergency shutdown CAN communication counter alarm | i * 200 + 326 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_EMCR_EMERGENCY_SHUTDOWN_SIGNAL_COUNTER_FAULT | RBMS_EMCR_EMERGENCY_SHUTDOWN_SIGNAL_COUNTER_FAULT
簇 (i+1) 紧急关断信号CAN通信CRC告警 String (i+1) emergency shutdown CAN communication CRC alarm | i * 200 + 327 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_EMCR_EMERGENCY_SHUTDOWN_SIGNAL_CRC_FAULT | RBMS_EMCR_EMERGENCY_SHUTDOWN_SIGNAL_CRC_FAULT
簇 (i+1) 紧急关断信号CAN通信超时告警 String (i+1) emergency shutdown CAN communication timeout alarm | i * 200 + 328 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_EMCR_EMERGENCY_SHUTDOWN_SIGNAL_TIMEOUT_FAULT | RBMS_EMCR_EMERGENCY_SHUTDOWN_SIGNAL_TIMEOUT_FAULT
簇 (i+1) 电芯电压与Battery电压不匹配告警 String (i+1) cell voltage does not match battery voltage alarm | i * 200 + 329 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_HVSH_CELL_SUM_VOLTAGE_WITH_BATTERY_MISMTCH_FAULT | RBMS_HVSH_CELL_SUM_VOLTAGE_WITH_BATTERY_MISMTCH_FAULT
簇 (i+1) 绝缘负对地电压无效告警 String (i+1) negative insulation to ground voltage invalid alarm | i * 200 + 330 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_ISOH_INVALID_ISOLATION_NEGV_FAULT | RBMS_ISOH_INVALID_ISOLATION_NEGV_FAULT
簇 (i+1) 绝缘正对地电压无效告警 String (i+1) positive insulation to ground voltage invalid alarm | i * 200 + 331 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_ISOH_INVALID_ISOLATION_POSV_FAULT | RBMS_ISOH_INVALID_ISOLATION_POSV_FAULT
簇 (i+1) 高压绝缘低轻度告警 String (i+1) high-voltage insulation low slight alarm | i * 200 + 332 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_ISOH_ISOLATION_LOW_LEVEL3_FAULT | RBMS_ISOH_ISOLATION_LOW_LEVEL3_FAULT
簇 (i+1) 高压绝缘低中度告警 String (i+1) high-voltage insulation low medium alarm | i * 200 + 333 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_ISOH_ISOLATION_LOW_LEVEL2_FAULT | RBMS_ISOH_ISOLATION_LOW_LEVEL2_FAULT
簇 (i+1) RBMS供电电压过高告警 String (i+1) RBMS supply voltage too high alarm | i * 200 + 334 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_LVPH_24V_INTERNAL_POWER_SUPPLY_OVER_VOLTAGE_FAULT | RBMS_LVPH_24V_INTERNAL_POWER_SUPPLY_OVER_VOLTAGE_FAULT
簇 (i+1) RBMS供电电压过低告警 String (i+1) RBMS supply voltage too low alarm | i * 200 + 335 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_LVPH_24V_INTERNAL_POWER_SUPPLY_UNDER_VOLTAGE_FAULT | RBMS_LVPH_24V_INTERNAL_POWER_SUPPLY_UNDER_VOLTAGE_FAULT
簇 (i+1) 电流传感器供电电压过高告警 String (i+1) current sensor supply voltage too high alarm | i * 200 + 336 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_LVPH_CURRENT_SENSOR_POWER_SUPPLY_OVER_VOLTAGE_FAULT | RBMS_LVPH_CURRENT_SENSOR_POWER_SUPPLY_OVER_VOLTAGE_FAULT
簇 (i+1) 电流传感器供电电压过低告警 String (i+1) current sensor supply voltage too low alarm | i * 200 + 337 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_LVPH_CURRENT_SENSOR_POWER_SUPPLY_UNDER_VOLTAGE_FAULT | RBMS_LVPH_CURRENT_SENSOR_POWER_SUPPLY_UNDER_VOLTAGE_FAULT
簇 (i+1) 高压采样芯片供电电压过低告警 String (i+1) high-voltage sampling chip supply voltage too low alarm | i * 200 + 338 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_LVPH_HIGH_VOLTAGE_SENSOR_POWER_SUPPLY_UNDER_VOLTAGE_FAULT | RBMS_LVPH_HIGH_VOLTAGE_SENSOR_POWER_SUPPLY_UNDER_VOLTAGE_FAULT
簇 (i+1) 继电器供电电压过高告警 String (i+1) relay supply voltage too high alarm | i * 200 + 339 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_LVPH_RELAY_POWER_SUPPLY_OVER_VOLTAGE_FAULT | RBMS_LVPH_RELAY_POWER_SUPPLY_OVER_VOLTAGE_FAULT
簇 (i+1) 继电器供电电压过低告警 String (i+1) relay supply voltage too low alarm | i * 200 + 340 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_LVPH_RELAY_POWER_SUPPLY_UNDER_VOLTAGE_FAULT | RBMS_LVPH_RELAY_POWER_SUPPLY_UNDER_VOLTAGE_FAULT
簇 (i+1) RBMS供电电压超范围告警 String (i+1) RBMS supply voltage out of range alarm | i * 200 + 341 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_LVPS_24V_INTERNAL_POWER_SUPPLY_OVERORUNDER_VOLTAGE_FAULT | RBMS_LVPS_24V_INTERNAL_POWER_SUPPLY_OVERORUNDER_VOLTAGE_FAULT
簇 (i+1) 电流传感器供电电压超范围告警 String (i+1) current sensor supply voltage out of range alarm | i * 200 + 342 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_LVPS_CURRENT_SENSOR_POWER_SUPPLY_OVERORUNDER_VOLTAGE_FAULT | RBMS_LVPS_CURRENT_SENSOR_POWER_SUPPLY_OVERORUNDER_VOLTAGE_FAULT
簇 (i+1) 继电器供电电压超范围告警 String (i+1) relay supply voltage out of range alarm | i * 200 + 343 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_LVPS_RELAY_POWER_SUPPLY_OVERORUNDER_VOLTAGE_FAULT | RBMS_LVPS_RELAY_POWER_SUPPLY_OVERORUNDER_VOLTAGE_FAULT
簇 (i+1) MCU芯片ADC模块告警 String (i+1) MCU chip ADC module alarm | i * 200 + 344 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_MCUD_CHIP_ADC_FAULT | RBMS_MCUD_CHIP_ADC_FAULT
簇 (i+1) MCU芯片CAN模块告警 String (i+1) MCU chip CAN module alarm | i * 200 + 345 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_MCUD_CHIP_CAN_FAULT | RBMS_MCUD_CHIP_CAN_FAULT
簇 (i+1) MCU芯片GPIO模块告警 String (i+1) MCU chip GPIO module alarm | i * 200 + 346 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_MCUD_CHIP_GPIO_FAULT | RBMS_MCUD_CHIP_GPIO_FAULT
簇 (i+1) MCU芯片SPI模块告警 String (i+1) MCU chip SPI module alarm | i * 200 + 347 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_MCUD_CHIP_SPI_FAULT | RBMS_MCUD_CHIP_SPI_FAULT
簇 (i+1) MCU初始化告警 String (i+1) MCU initialization alarm | i * 200 + 348 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_MCUD_INIT_FAULT | RBMS_MCUD_INIT_FAULT
簇 (i+1) RTC时间无效告警 String (i+1) RTC time invalid alarm | i * 200 + 349 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_SGPC_RTC_TIME_INVALID_FAULT | RBMS_SGPC_RTC_TIME_INVALID_FAULT
簇 (i+1) SOC差异过大告警 String (i+1) SOC difference too large alarm | i * 200 + 350 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data | RBMS_SOCA_SOC_DIFFER_VALUE_OVER_HIGH_FAULT | RBMS_SOCA_SOC_DIFFER_VALUE_OVER_HIGH_FAULT
簇 (i+1) 气溶胶告警 String (i+1) Aerosol alarm | i * 200 + 351 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_ACIS_AEROSOL_FAULT
簇 (i+1) 急停告警 String (i+1) Estop alarm | i * 200 + 352 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_ACIS_ESTOP_FAULT
簇 (i+1) 气溶胶2告警 String (i+1) Aerosol2 alarm | i * 200 + 353 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_ACIS_AEROSOL2_FAULT
簇 (i+1) 消防中度告警 String (i+1) Fire extinguisher alert alarm | i * 200 + 354 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_ACIS_FIRE_EXTINGUISHER_ALARM_FAULT
簇 (i+1) 消防轻度告警 String (i+1) Fire extinguisher warn alarm | i * 200 + 355 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_ACIS_FIRE_EXTINGUISHER_WARN_FAULT
簇 (i+1) QF1断路器告警 String (i+1) QF1 breaker alarm | i * 200 + 356 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_ACIS_QF1_BREAKER_FAULT
簇 (i+1) 水浸告警告警 String (i+1) Water flood alarm | i * 200 + 357 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_ACIS_WATER_FLOOD_FAULT
簇 (i+1) 与EMS通讯丢失告警 String (i+1) EMS to BMS communication lost alarm | i * 200 + 358 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data
簇 (i+1) 与电表通讯丢失告警 String (i+1) Energymeter to BMS communication lost alarm | i * 200 + 359 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data
簇 (i+1) 与PCS通讯丢失告警 String (i+1) PCS to BMS communication lost alarm | i * 200 + 360 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data
簇 (i+1) 与UPS通讯丢失告警 String (i+1) UPS to BMS communication lost alarm | i * 200 + 361 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data
簇 (i+1) 水冷机轻度告警 String (i+1) TMS slight alarm | i * 200 + 362 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_THMC_TMS_LEVEL3_FAULT
簇 (i+1) 水冷机中度告警 String (i+1) TMS medium alarm | i * 200 + 363 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_THMC_TMS_LEVEL2_FAULT
簇 (i+1) 水冷机重度告警 String (i+1) TMS serious alarm | i * 200 + 364 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_THMC_TMS_LEVEL1_FAULT
簇 (i+1) 水冷机组工作模式不匹配告警 String (i+1) TMS request and work mode different alarm | i * 200 + 365 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_THMC_TMS_REQUEST_DIFF_FAULT
簇 (i+1) 与TMS通讯丢失告警 String (i+1) TMS to BMS communication lost alarm | i * 200 + 366 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_TMCR_TMS_TO_BMS_COMMUNICATION_LOST_FAULT
簇 (i+1) 与 IO模块通信丢失告警 String (i+1) IO module to BMS communication lost alarm | i * 200 + 367 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_EMCR_IOModule_TO_BMS_COMMUNICATION_LOST_FAULT
簇 (i+1) 与除湿机通讯节点丢失告警 String (i+1) Dehumidifier to BMS communication lost alarm | i * 200 + 368 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_EMCR_DEHUMIDIFIER_TO_BMS_COMMUNICATION_LOST_FAULT
簇 (i+1) 散热风扇告警 String (i+1) Cooling fan alarm | i * 200 + 369 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_ACIS_COOL_FAN_FAULT
簇 (i+1) 烟感告警 String (i+1) Smoke detector alarm | i * 200 + 370 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_ACIS_SMOKE_FEEDBACK_FAULT
簇 (i+1) 温感告警 String (i+1) Heat detector alarm | i * 200 + 371 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_ACIS_TEMP_FEEDBACK_FAULT
簇 (i+1) 电流传感器通讯丢失轻微告警 String (i+1) current sensor communication loss slight alarm | i * 200 + 372 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_BTCS_CANMSG_TIMEOUT_LEVEL3_FAULT
簇 (i+1) 电流传感器硬件轻微告警 String (i+1) current sensor hardware slight alarm | i * 200 + 373 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_BTCS_CANBATI_IMPLY_LEVEL3_FAULT
簇 (i+1) 电流传感器零漂轻微告警 String (i+1) current sensor zero drift slight alarm | i * 200 + 374 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_BTCS_CANBATI_ZERODRIFT_LEVEL3_FAULT
簇 (i+1) 电流传感器CRC轻微告警 String (i+1) current sensor CRC slight alarm | i * 200 + 375 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_BTCS_CANMSG_CRCRES_LEVEL3_FAULT
簇 (i+1) 电流传感器值差异过大告警 String (i+1) current sensor value difference too large alarm | i * 200 + 376 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_BTCS_BATIDIFFHIGH_FAULT
簇 (i+1) 主正连接母线断路告警 String (i+1) Main positive bus broken alarm | i * 200 + 377 |  | 1 | 1 | 0 |  | 0-无告警， 1-告警/0 - No alarm, 1 - Alarm | Rack | Fault | RBMS_Fault_Data |  | RBMS_HVSH_MAIN_POSITIVE_BUS_BROKEN_FAULT

## 保持寄存器
Field | Start address (decimal) | DataType | Bit Length (Bit) | Resolution | offset | Remark
预留 Reserved | 500 | UINT | 16 | 1 | 0
系统故障复位 System fault reset | 501 | UINT | 16 | 1 | 0 | 【此功能暂未实现】 0：不复归； 1：复归； 其它值：无效 0: Do not reset； 1: Reset； other values: Invalid
预留 Reserved | 502 | UINT | 16 | 1 | 0
EMS控制BMS系统上下电指令 System power up and down control command from EMS | 503 | UINT | 16 | 1 | 0 | 【此功能暂未实现】 注： 默认不使用， 供电后堆自主上电， 若需要， 请于项目对接阶段明确 0：不操作；1：上高压；2：下高压； 其它值：无效 Note: It is not used by default, and the reactor is powered on automatically after power supply. If necessary, please specify in the project docking stage 0: No operation； 1: Power on； 2: Power off； Other values: Invalid
预留 Reserved | 504-523 | UINT | 16 | 1 | 0
RTC-年 RTC-Year | 524 | UINT | 16 | 1 | 2000 | 年 数据范围： 0~100/ Year data field:0~100
RTC-月 RTC-Month | 525 | UINT | 16 | 1 | 0 | 月 数据范围： 1~12/ Month data field:1~12
RTC-日 RTC-Day | 526 | UINT | 16 | 1 | 0 | 日 数据范围： 1~31/ Day data field:1~31
RTC-时 RTC-Hour | 527 | UINT | 16 | 1 | 0 | 时 数据范围： 0~23/ Hour data field:0~23
RTC-分 RTC-Minute | 528 | UINT | 16 | 1 | 0 | 分 数据范围： 0~59/ Minute data field:0~59
RTC-秒 RTC-Second | 529 | UINT | 16 | 1 | 0 | 秒 数据范围： 0~59/ Second data field:0~59

## 输入寄存器
Field | Start address (decimal) | DataType | Bit Length (Bit) | Resolution | offset | Unit | Remark | Layer | Classification | Signal Source | Mapping Signal BMS20/BMS23
电池堆直流母线电压 System DC Bus voltage | 1 | UINT | 16 | 0.5 | 0 | V |  | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_DCBusV
电池堆直流母线电流 System DC Bus current | 2 | UINT | 16 | 0.125 | -4000 | A |  | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_TotalDCCur
电池堆SOC System SOC | 3 | UINT | 16 | 0.5 | 0 | % | 堆显示SOC | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_SOC
电池堆SOH System SOH | 4 | UINT | 16 | 1 | 0 | % | 堆显示SOH | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_SOH
最高电池电压 Maximum battery voltage | 5 | UINT | 16 | 1 | 0 | mV |  | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_MaxCellV
最高电压电池组号 Maximum voltage battery Sring No | 6 | UINT | 16 | 1 | 0 | / | 最大电压Rack位置 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_MaxVCellRackNr
最高电压电池所在组中的点号 Point number in maximum voltage battery Sring | 7 | UINT | 16 | 1 | 0 | / | 最大电压电芯位置 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_MaxVCellNr
最低电池电压 Minimum battery voltage | 8 | UINT | 16 | 1 | 0 | mV |  | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_MinCellV
最低电压电池组号 Minimum voltage battery Sring No | 9 | UINT | 16 | 1 | 0 | / | 最小电压Rack位置 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_MinVCellRackNr
最低电压电池所在组中的点号 Point number in minimum voltage battery Sring | 10 | UINT | 16 | 1 | 0 | / | 最小电压电芯位置 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_MinVCellNr
最高电池温度 Maximum battery temperature | 11 | UINT | 16 | 0.1 | -40 | ℃ |  | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_MaxCellT
最高温度电池组号 Maximum temperature battery Sring No | 12 | UINT | 16 | 1 | 0 | / | 最高电芯温度Rack位置 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_MaxTCellRackNr
最高温度电池所在组中的点号 Point number in maximum temperature battery Sring | 13 | UINT | 16 | 1 | 0 | / | 最高电芯温度位置 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_MaxTCellNr
最低电池温度 Minimum battery temperature | 14 | UINT | 16 | 0.1 | -40 | ℃ |  | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_MinCellT
最低温度电池组号 Minimum temperature battery Sring No | 15 | UINT | 16 | 1 | 0 | / | 最高电芯温度Rack位置 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_MinTCellRackNr
最低温度电池所在组中的点号 Point number in minimum temperature battery Sring | 16 | UINT | 16 | 1 | 0 | / | 最高电芯温度位置 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_MinTCellNr
堆累计充电电量 System accumulated charging energy | 17 | UINT | 32 | 1 | 0 | kWh |  | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_AccuChrgE
堆累计放电电量 System accumulated discharging energy | 19 | UINT | 32 | 1 | 0 | kWh |  | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_AccuDisChrgE
堆最近一次充电电量 System latest charge energy | 21 | UINT | 16 | 1 | 0 | kWh | 最近一次充电能量 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_LstChEkWh
堆最近一次放电电量 System latest discharge energy | 22 | UINT | 16 | 1 | 0 | kWh | 最近一次放电能量 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_LstDchEkWh
预留 Reserved | 23 | UINT | 16 |  |  |  |  | Bank
堆可充电量 System chargeable energy | 24 | UINT | 16 | 0.125 | 0 | kWh |  | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_MaxChrgE
堆可放电量 System dischargeable energy | 25 | UINT | 16 | 0.125 | 0 | kWh |  | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_MaxDisChrgE
允许最大放电功率 Allowable maximum discharge power | 26 | UINT | 16 | 0.125 | 0 | kW | 持续放电功率限制 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_MaxContDisChrgPower
允许最大充电功率 Allowable maximum charge power | 27 | UINT | 16 | 0.125 | 0 | kW | 持续充电功率限制 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_MaxContChrgPower
允许最大放电电流 Allowable maximum discharge current | 28 | UINT | 16 | 0.125 | 0 | A | 持续放电电流限制 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_MaxContDisChrgCur
允许最大充电电流 Allowable maximum charge current | 29 | UINT | 16 | 0.125 | 0 | A | 持续充电电流限制 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_MaxContChrgCur
电芯平均运行温度 Cell operating average temperature | 30 | UINT | 16 | 0.1 | -40 | ℃ |  | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_AvgCellT
BMS堆当前工作状态 System Status | 31 | UINT | 16 | 1 | 0 | / | 0: 地址分配 1: 未连接 2: 预留 3: 已连接 4: 预留 5: SOC保护 6: 关机中 99: 故障 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_BatSt
BMS充放电状态 Charge discharge state | 32 | UINT | 16 | 1 | 0 | / | 1: 未连接 2: 满放 3: 放电 4: 充电 5: 满充 6: 静置 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_ChSt
堆内电池组数 String number | 33 | UINT | 16 | 1 | 0 | / | 堆内使能簇数 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_RackEnaNbr
堆内在线电池组数 Online string number | 34 | UINT | 16 | 1 | 0 | / | 堆内Online簇数 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_RackOnlineNbr
堆连接失败原因 Connection failure reason | 35 | UINT | 16 | 1 | 0 | / | Bit0: 存在使能簇有严重故障 Bit1: Bank存在严重故障 Bit2: 存在使能簇绝缘未完成 Bit3: 簇间压差过大 Bit4: Bank为本地模式 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_ConFail
堆心跳信号 System heart beat | 36 | UINT | 16 | 1 | 0 | / | 数据范围: 0~65535 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_StrCtrlHb
存在严重故障的Rack位置 Positions of string with serious alarm | 37 | UINT | 16 | 1 | 0 | / | 系统中各簇的严重故障标志位(0表示正常，1表示严重故障) Bit0: Rack1严重故障 Bit1: Rack2严重故障 Bit2: Rack3严重故障 Bit3: Rack4严重故障 ... Bit15: Rack16严重故障 | Bank | SumInfo | BBMS_SumInfo_Data | BBMS_RackFltLvl1Nbr
系统下高压指令 System power down command | 38 | UINT | 16 | 1 | 0 | / | 0: 无外部下高压指令； 1: BMS自行判断下高压； 2: EMS下高压指令； 3: PCS下高压指令； 4: 消防主机下高压指令； 5: 预留位置； | Bank | SumInfo | BBMS_SumInfo_Data
预留 Reserved | 39-99 | [6 empty] | Bank
簇 (i+1) 电池充放电状态 String(i+1)charge discharge state | i * 3000 + 100 | UINT | 16 | 1 | 0 | / | 1: 未连接 2: 满放 3: 放电 4: 充电 5: 满充 6: 静置 | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_ChaSt
簇 (i+1) 最大故障等级 String (i+1) maximum alarm level | i * 3000 + 101 | UINT | 16 | 1 | 0 | / | 1: 重度告警 2: 中度告警 3: 轻度告警 | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_BMSMaxFltLevel
簇 (i+1) 允许充电最大功率 String (i+1) maximum allowable charging power | i * 3000 + 102 | UINT | 16 | 0.125 | 0 | kW |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_SoFPulseChrgPwr
簇 (i+1) 允许放电最大功率 String (i+1) maximum allowable discharging power | i * 3000 + 103 | UINT | 16 | 0.125 | 0 | kW |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_SoFPulseDisChrgPwr
簇 (i+1) 允许充电最大电流 String (i+1) maximum allowable charging current | i * 3000 + 104 | UINT | 16 | 0.125 | 0 | A |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_SoFContChrgCurr
簇 (i+1) 允许放电最大电流 String (i+1) maximum allowable discharging current | i * 3000 + 105 | UINT | 16 | 0.125 | 0 | A |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_SoFContDisChrgCurr
簇 (i+1) 组直流母线电压 String (i+1) DC bus voltage | i * 3000 + 106 | UINT | 16 | 0.5 | 0 | V |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_DCBusV
簇 (i+1) 组电流 String (i+1) Current | i * 3000 + 107 | UINT | 16 | 0.125 | -2000 | A |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_A
簇 (i+1) 组 SOC String (i+1) SOC | i * 3000 + 108 | UINT | 16 | 0.5 | 0 | % |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_SoC
簇 (i+1) 组 SOH String (i+1) SOH | i * 3000 + 109 | UINT | 16 | 1 | 0 | % |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_SoH
簇 (i+1) 组绝缘电阻 String (i+1) insulation resistance | i * 3000 + 110 | UINT | 16 | 1 | 0 | KΩ |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_IsoR
簇 (i+1) 平均单体电压 String (i+1) average cell voltage | i * 3000 + 111 | UINT | 16 | 1 | 0 | mV |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_CellVAvg
簇 (i+1) 平均单体温度 String (i+1) average cell temperature | i * 3000 + 112 | UINT | 16 | 0.1 | -40 | ℃ |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_ModTmpAvg
簇 (i+1) 最高单体电压 String (i+1) maximum cell voltage | i * 3000 + 113 | UINT | 16 | 1 | 0 | mV |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_CellVMax
簇 (i+1) 最高单体电压对应点号 Cell number of String (i+1) maximum cell voltage | i * 3000 + 114 | UINT | 16 | 1 | 0 | / |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_CellVMaxPstn
簇 (i+1) 最低单体电压 String (i+1) minimum cell voltage | i * 3000 + 115 | UINT | 16 | 1 | 0 | mV |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_CellVMin
簇 (i+1) 最低单体电压对应点号 String (i+1) number of minimum cell voltage | i * 3000 + 116 | UINT | 16 | 1 | 0 | / |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_CellVMinPstn
簇 (i+1) 最高单体温度 String (i+1) maximum cell temperature | i * 3000 + 117 | UINT | 16 | 0.1 | -40 | ℃ |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_ModTmpMax
簇 (i+1) 最高单体温度对应点号 String (i+1) number of maximum cell temperature | i * 3000 + 118 | UINT | 16 | 1 | 0 | / |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_ModTmpMaxPstn
簇 (i+1) 最低单体温度 String (i+1) minimum cell temperature | i * 3000 + 119 | UINT | 16 | 0.1 | -40 | ℃ |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_ModTmpMin
簇 (i+1) 最低单体温度对应点号 String (i+1) number of minimum cell temperature | i * 3000 + 120 | UINT | 16 | 1 | 0 | / |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_ModTmpMinPstn
簇 (i+1) 最高单体 SOC String (i+1) maximum cell SOC | i * 3000 + 121 | UINT | 16 | 0.01 | 0 | % |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_SysMaxSOC
簇 (i+1) 最高单体 SOC 对应点号 String (i+1) number of maximum cell SOC | i * 3000 + 122 | UINT | 16 | 1 | 0 | / |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_CellVMaxPstn
簇 (i+1) 最低单体 SOC String (i+1) minimum cell SOC | i * 3000 + 123 | UINT | 16 | 0.01 | 0 | % |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_SysMinSOC
簇 (i+1) 最低单体 SOC 对应点号 String (i+1) number of minimum cell SOC | i * 3000 + 124 | UINT | 16 | 1 | 0 | / |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_CellVMinPstn
簇 (i+1) 极柱最大温度 String (i+1) pole maximum temperature | i * 3000 + 125 | UINT | 16 | 0.1 | -40 | ℃ |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_MaxPoleTDegC
簇 (i+1) 极柱最大温度编号 String (i+1) pole maximum temperature index | i * 3000 + 126 | UINT | 16 | 1 | 0 | / |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_MaxPoleTIdxNbr
簇 (i+1) 极柱最小温度 String (i+1) pole minimum temperature | i * 3000 + 127 | UINT | 16 | 0.1 | -40 | ℃ |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_MinPoleTDegC
簇 (i+1) 极柱最小温度编号 String (i+1) pole minimum temperature index | i * 3000 + 128 | UINT | 16 | 1 | 0 | / |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_MinPoleTIdxNbr
簇 (i+1) 极柱最大温度对应模组号 String (i+1) pole maximum temperature module number | i * 3000 + 129 | UINT | 16 | 1 | 0 | / |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_MaxPoleTMdulIdxNbr
簇 (i+1) 极柱最小温度对应模组号 String (i+1) pole minimum temperature module number | i * 3000 + 130 | UINT | 16 | 1 | 0 | / |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_MinPoleTMdulIdxNbr
簇 (i+1) 极柱平均温度 String (i+1) pole average temperature | i * 3000 + 131 | UINT | 16 | 0.1 | -40 | ℃ |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_AvgPoleTDegC
簇 (i+1) 累计充电电量 String (i+1) accumulated charging energy | i * 3000 + 132 | UINT | 32 | 1 | 0 | kWh |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_AccuChrgkWh
簇 (i+1) 累计放电电量 String (i+1) accumulated discharging energy | i * 3000 + 134 | UINT | 32 | 1 | 0 | kWh |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_AccuDisChrgkWh
簇 (i+1) 最近一次充电电量 String (i+1) latest charge energy | i * 3000 + 136 | UINT | 16 | 0.1 | 0 | kWh | 最近一次簇充电能量 | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_LstChEkWh
簇 (i+1) 最近一次放电电量 String (i+1) latest discharge energy | i * 3000 + 137 | UINT | 16 | 0.1 | 0 | kWh | 最近一次簇放电能量 | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_LstDchEkWh
簇 (i+1) 可充电量 String (i+1) rechargeable capacity | i * 3000 + 138 | UINT | 16 | 0.125 | 0 | kWh |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_SoEC
簇 (i+1) 可放电量 String (i+1) discharge capacity | i * 3000 + 139 | UINT | 16 | 0.125 | 0 | kWh |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_SoED
簇 (i+1) 充电电压限制 String (i+1) charge Voltage Limit | i * 3000 + 140 | UINT | 16 | 0.1 | 0 | V |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_PCSChVoltLim
簇 (i+1) 放电电压限制 String (i+1) discharge Voltage Limit | i * 3000 + 141 | UINT | 16 | 0.1 | 0 | V |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_PCSDchVoltLim
簇 (i+1) SOP String (i+1) SOP | i * 3000 + 142 | UINT | 16 | 0.1 | 0 | kW |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_PCSSOP
簇 (i+1) bms 状态 String (i+1) bms status | i * 3000 + 143 | UINT | 16 | 1 | 0 | Nbr |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_PCSBMSSt
簇 (i+1) 工作状态 String (i+1) Status | i * 3000 + 144 | UINT | 16 | 1 | 0 | / | Bit0[1]: Rack Enable Status;Rack使能状态 Signal; 0X0-Disabled; 0X1-Enabled; Bit1[1]: Rack Online Status;Rack在线状态 Signal; 0X0-Offline; 0X1-Online; Bit2[1]: Rack Control Mode Status;Rack控制模式 Signal; 0X0-BMS Control; 0X1-Debug; Bit3[1]: Overall Balancing Status;均衡状态 Signal; 0X0-Stop; 0X1-Ongoing; Bit4[0]: Fault Hardline Status;故障路线状态 Signal; 0X0- Activitied; 0X1- Disactivitied; Bit5[1]: Green Light Status;绿灯状态 Signal; 0X0-Off; 0X1-On; Bit6[1]: Yellow Light Status;黄灯状态 Signal; 0X0-Off; 0X1-On; Bit7[1]: Red Light Status;红灯状态 Signal; 0X0-Off; 0X1-On; | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_St
簇 (i+1) 预留 String (i+1) Reserved | i * 3000 + 145 to 200
簇 (i+1) 单体电压 (j+1) String (i+1) cell voltage (j+1) | i * 3000 + 201 + j | UINT | 16 | 1 | 0 | mV |  | Rack | CellV-Array | RBMS_Volt_Data | RBMS_CellV
簇 (i+1) 单体温度 (j+1) String (i+1) cell temperature (j+1) | i * 3000 + 901 + j | UINT | 16 | 0.1 | -40 | ℃ |  | Rack | CellT-Array | RBMS_Temp_Data | RBMS_ModTmp
簇 (i+1) 极柱温度 (j+1) String (i+1) pole temperature (j+1) | i * 3000 + 1601 + j | UINT | 16 | 0.1 | -40 | ℃ |  | Rack | PoleT-Array | RBMS_Temp_Data | RBMS_PoleTDegC
簇 (i+1) PACK连接器温度(j+1) String (i+1) pack connector temperature (j+1) | i * 3000 + 1761 + j | UINT | 16 | 0.1 | -40 | ℃ |  | Rack | ConnectT-Array | RBMS_Temp_Data | RBMS_PackPosNegConnTDegC
预留 Reserved | i * 3000 + 1801 to 2200
簇 (i+1) 继电器/干接点状态 String (i+1) contactor status | i * 3000 + 2201 | UINT | 16 | 1 | 0 | / | Bit0: Main Negative Contactor Status (0X0: Open 断开; 0X1: Closed 闭合) Bit1: Main Positive Contactor Status (0X0: Open 断开; 0X1: Closed 闭合) Bit2: Precharge Contactor Status (0X0: Open 断开; 0X1: Closed 闭合) Bit3: Fuse Open Status Bit4: Control Box Heater Status Bit5: QF Switch Status (断路器QF) Bit6: QS Switch Status (隔离开关QS) (0X0: Closed 闭合; 0X1: Open 断开) Bit7: Hv Interlock Status(MSD) (0X0: Closed 闭合; 0X1: Open 断开) Bit8-9: Control Box Cooling Fan Status Bit10: EPO Input Status (0X0: Closed 闭合; 0X1: Open 断开) Bit11: Fire Extinguisher Warn Status Bit12: Fire Extinguisher Fault Status Bit13: Fire Extinguisher Actuator Status Bit14: Isolation finished flag Bit15: Door Open Status (0X0: Closed 闭合; 0X1: Open 断开) | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_ConSt
簇 (i+1) 高压连接失败原因 String (i+1) connection failure reason | i * 3000 + 2202 | UINT | 16 | 1 | 0 | / | Bit0: ISO Not Finished Bit1: High voltage Invalid (HvLnkPosV or HvBatV) Bit2: ISO Failure Bit3: Contactor Failure Bit4: Current Invalid Bit5: Precharge Failure Bit6: Relay Fault Bit7: Safty Fault Bitx8: String Disactived Bit9: HvPowupCmd Disconnect Bit10: Voltage difference exceeds the threshold Bit11: Reach Precharge Max Time Bit12: PrechFailFlg Bit13: Precharge Not Finished Bit14: The conditions for allowing precharging are not met Bit15: EPO open | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_ConFail
簇 (i+1) 高压箱温度T0 String (i+1) HV Box Temperature0 | i * 3000 + 2203 | UINT | 16 | 0.1 | -40 | ℃ |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_CtlBoxT0DegC
簇 (i+1) 高压箱温度T1 String (i+1) HV Box Temperature0 | i * 3000 + 2204 | UINT | 16 | 0.1 | -40 | ℃ |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_CtlBoxT1DegC
簇 (i+1) 高压箱温度T2 String (i+1) HV Box Temperature0 | i * 3000 + 2205 | UINT | 16 | 0.1 | -40 | ℃ |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_CtlBoxT2DegC
簇 (i+1) 高压箱温度T3 String (i+1) HV Box Temperature0 | i * 3000 + 2206 | UINT | 16 | 0.1 | -40 | ℃ |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_CtlBoxT3DegC
簇 (i+1) 继电器控制状态 String (i+1) relay control state | i * 3000 + 2207 | UINT | 16 | 1 | 0 | / | 0: Initial 1: ClsMainNeg 2: ClsPrech 3: ClsMainPos 4: Online 5: WaitForCurrDwn 6: OpenMainPos 7: OpenMainNeg 8: DlyForNxtPowup 9: Service | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_RlyCtrlSeqStState
簇 (i+1) 绝缘禁止原因 String (i+1) insulation disable reason | i * 3000 + 2208 | UINT | 16 | 1 | 0 | / | 0x0: 正常 0x1: 上位机禁止绝缘 0x2: 绝缘相关电压有效性无效 0x3: 高压禁止绝缘 0x4: XCP配置禁止绝缘 | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_IslnInhibitNbr
簇 (i+1) 绝缘总压 String (i+1) insulation total voltage | i * 3000 + 2209 | UINT | 16 | 1 | 0 | V |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_IslnFinalBatV
簇 (i+1) 绝缘正对地电压 String (i+1) insulation positive to ground voltage | i * 3000 + 2210 | UINT | 16 | 1 | 0 | V |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_IslnFinalPosV
簇 (i+1) 绝缘负对地电压 String (i+1) insulation negative to ground voltage | i * 3000 + 2211 | UINT | 16 | 1 | 0 | V |  | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_IslnFinalNegV
簇 (i+1) 绝缘测量状态 String (i+1) insulation measurement state | i * 3000 + 2212 | UINT | 16 | 1 | 0 | / | 0x0: Initial 0x1: Pending 0x2: Finished 0x3: Inhibit | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_IslnMeastStState
簇 (i+1) RBMS采样有效性标志 String (i+1) RBMS sampling validity flag | i * 3000 + 2213 | UINT | 16 | 1 | 0 | / | Bit0: Cell Temperature General Validity;电芯温度概要有效性 Signal; 0X0-Invalid; 0X1-Valid; Bit1: Cell Voltage General Validity;电芯电压概要有效性 Signal; 0X0-Invalid; 0X1-Valid; Bit2: Battery Current Validity;簇电流有效性 Signal; 0X0-Invalid; 0X1-Valid; Bit3: LinkPosVoltage Validity;LinkPos电压有效性 Signal; 0X0-Invalid; 0X1-Valid; | Rack | SumInfo | RBMS_SumInfo_Data | RBMS_GenlVldFlg
簇 (i+1) 满充修正标志位 String (i+1) full charge correction flag | i * 3000 + 2214 | UINT | 16 | 1 | 0 | / | bit0: Display SOC full charge correction flag(0X0: hold 保持 ; 0X1: correction修正) bit1: Real SOC full charge correction flag(0X0: hold 保持 ; 0X1: correction修正) | Rack | SOXdebug | RBMS_SOXdebugData1
簇 (i+1) 满放修正标志位 String (i+1) full discharge correction flag | i * 3000 + 2215 | UINT | 16 | 1 | 0 | / | bit0: Display SOC full discharge correction flag(0X0: hold 保持 ; 0X1: correction修正) bit1: Real SOC full discharge correction flag(0X0: hold 保持 ; 0X1: correction修正) | Rack | SOXdebug | RBMS_SOXdebugData1
簇 (i+1) 累计充电容量 String (i+1) accumulated charging capacity | i * 3000 + 2216 | UINT | 32 | 0.0625 | 0 | Ah |  | Rack | SOXdebug | RBMS_SOXdebugData1
簇 (i+1) 累计放电容量 String (i+1) accumulated discharging capacity | i * 3000 + 2218 | UINT | 32 | 0.0625 | 0 | Ah |  | Rack | SOXdebug | RBMS_SOXdebugData1
簇 (i+1) 上次下电休眠时间 String (i+1) last power-down seep time | i * 3000 + 2220 | UINT | 32 | 1 | 0 | min |  | Rack | SOXdebug | RBMS_SOXdebugData1
簇 (i+1) 历史休眠时间 String (i+1) history sleep time | i * 3000 + 2222 | UINT | 32 | 1 | 0 | min |  | Rack | SOXdebug | RBMS_SOXdebugData1
簇 (i+1) 历史运行时间 String (i+1) history run time | i * 3000 + 2224 | UINT | 32 | 1 | 0 | min |  | Rack | SOXdebug | RBMS_SOXdebugData1
簇 (i+1) 累计循环次数 String (i+1) accumulated cycle number | i * 3000 + 2226 | UINT | 16 | 1 | 0 | / |  | Rack | SOXdebug | RBMS_SOXdebugData1
簇 (i+1) SOH标定指示 String (i+1) SOH calibration indicator | i * 3000 + 2227 | UINT | 16 | 1 | 0 | / |  | Rack | SOXdebug | RBMS_SOXdebugData1
簇 (i+1) SOH标定值 String (i+1) SOH calibration value | i * 3000 + 2228 | UINT | 16 | 1 | 0 | pct |  | Rack | SOXdebug | RBMS_SOXdebugData1
簇 (i+1) 高精度累积充电容量 String (i+1) high-precision accumulated charging capacity | i * 3000 + 2229 | UINT | 32 | 0.001 | 0 | mAh |  | Rack | SOXdebug | RBMS_SOXdebugData1
簇 (i+1) 高精度累积放电容量 String (i+1) high-precision accumulated discharging capacity | i * 3000 + 2231 | UINT | 32 | 0.001 | 0 | mAh |  | Rack | SOXdebug | RBMS_SOXdebugData1
簇 (i+1) 历史信息标定指示 String (i+1) history info calibration indicator | i * 3000 + 2233 | UINT | 16 | 1 | 0 | / |  | Rack | SOXdebug | RBMS_SOXdebugData1
簇 (i+1) SOC标定指示 String (i+1) SOC calibration indicator | i * 3000 + 2234 | UINT | 16 | 1 | 0 | / |  | Rack | SOXdebug | RBMS_SOXdebugData1
簇 (i+1) SOC标定值 String (i+1) SOC calibration value | i * 3000 + 2235 | UINT | 16 | 1 | 0 | pct |  | Rack | SOXdebug | RBMS_SOXdebugData1
簇 (i+1) 最大电压电芯对应温度 String (i+1) Vmax cell temperature | i * 3000 + 2236 | UINT | 16 | 0.1 | -40 | ℃ |  | Rack | SOXdebug | RBMS_SOXdebugData1
簇 (i+1) 最小电压电芯对应温度 String (i+1) Vmin cell temperature | i * 3000 + 2237 | UINT | 16 | 0.1 | -40 | ℃ |  | Rack | SOXdebug | RBMS_SOXdebugData1
簇 (i+1) 最大最小电压电芯对应温度有效性 String (i+1) Vmax & Vmin cell temperature validity flag | i * 3000 + 2238 | UINT | 16 | 1 | 0 | / | Bit0[1]: Vmax cell temperature validity;最大电压电芯温度有效性 (0X0-Invalid; 0X1-Valid) Bit1[1]: Vmin cell temperature validity;最小电压电芯温度有效性 (0X0-Invalid; 0X1-Valid) | Rack | SOXdebug | RBMS_SOXdebugData1
簇 (i+1) 真实SOH String (i+1) Real SOH | i * 3000 + 2239 | UINT | 16 | 0.01 | 0 | pct |  | Rack | SOXdebug | RBMS_SOXdebugData2
簇 (i+1) DFCL模块容量 String (i+1) DFCL module capacity | i * 3000 + 2240 | UINT | 16 | 0.1 | 0 | Ah |  | Rack | SOXdebug | RBMS_SOXdebugData2
簇 (i+1) DFCL模块SOH特征点SOC String (i+1) DFCL module SOH feature point SOC | i * 3000 + 2241 | UINT | 16 | 0.01 | 0 | pct |  | Rack | SOXdebug | RBMS_SOXdebugData2
簇 (i+1) DFCL模块SOH特征点标志位 String (i+1) DFCL module SOH feature point status | i * 3000 + 2242 | UINT | 16 | 1 | 0 | / |  | Rack | SOXdebug | RBMS_SOXdebugData2
簇 (i+1) DFCL模块SOH特征点容量 String (i+1) DFCL module SOH feature point capacity | i * 3000 + 2243 | UINT | 16 | 0.1 | -1500 | Ah |  | Rack | SOXdebug | RBMS_SOXdebugData2
簇 (i+1) DFCL模块SOH特征点时间 String (i+1) DFCL module SOH feature point time | i * 3000 + 2244 | UINT | 16 | 1 | 0 | day |  | Rack | SOXdebug | RBMS_SOXdebugData2
簇 (i+1) MFCL模块容量 String (i+1) MFCL module capacity | i * 3000 + 2245 | UINT | 16 | 0.1 | 0 | Ah |  | Rack | SOXdebug | RBMS_SOXdebugData2
簇 (i+1) Vmax节电芯MFCL模块中特征点目标计算值 String (i+1) Vmax cell MFCL module mid-feature point target value | i * 3000 + 2246 | UINT | 16 | 1 | 0 | / |  | Rack | SOXdebug | RBMS_SOXdebugData2
簇 (i+1) Vmin节电芯MFCL模块中特征点目标计算值 String (i+1) Vmin cell MFCL module mid-feature point target value | i * 3000 + 2247 | UINT | 16 | 1 | 0 | / |  | Rack | SOXdebug | RBMS_SOXdebugData2
簇 (i+1) 最大电压电芯SOC状态 String (i+1) Vmax cell SOC status | i * 3000 + 2248 | UINT | 16 | 1 | 0 | / | 0：AH(安时积分修正) 1：RVC(静置电压修正) 2：EDE(高精度动态修正) 3：FDC(满放修正) 4：FCC(满充修正) 5：SOC标定 6：NearFCC(非满充修正) 7：Near100FCC(非满充100修正) | Rack | SOXdebug | RBMS_SOXdebugData2
簇 (i+1) 最小电压电芯SOC状态 String (i+1) Vmin cell SOC status | i * 3000 + 2249 | UINT | 16 | 1 | 0 | / | 0：AH(安时积分修正) 1：RVC(静置电压修正) 2：EDE(高精度动态修正) 3：FDC(满放修正) 4：FCC(满充修正) 5：SOC标定 6：NearFCC(非满充修正) 7：Near100FCC(非满充100修正) | Rack | SOXdebug | RBMS_SOXdebugData2
簇 (i+1) 真实容量 String (i+1) real capacity | i * 3000 + 2250 | UINT | 16 | 0.1 | 0 | Ah |  | Rack | SOXdebug | RBMS_SOXdebugData2
簇 (i+1) 真实SOC String (i+1) real SOC | i * 3000 + 2251 | UINT | 16 | 0.01 | 0 | pct |  | Rack | SOXdebug | RBMS_SOXdebugData2
簇 (i+1) 显示SOC跟随策略状态 String (i+1) dispSOC follow strategy status | i * 3000 + 2252 | UINT | 16 | 1 | 0 | / |  | Rack | SOXdebug | RBMS_SOXdebugData2
簇 (i+1) DFCL与MFCL计算标志位 String (i+1) DFCL & MFCL calculation flag | i * 3000 + 2253 | UINT | 16 | 1 | 0 | / | Bit0：DFCL calculation flag ;DFCL模块容量计算标志位 Bit1：MFCL calculation flag ;MFCL模块容量计算标志位 Bit2：Vmax cell MFCL Point1 flag ; Vmax节电芯MFCL模块特征点1 Bit3：Vmin cell MFCL Point1 flag ; Vmin节电芯MFCL模块特征点1 Bit4：Vmax cell MFCL Point2 flag ; Vmax节电芯MFCL模块特征点2 Bit5：Vmin cell MFCL Point2 flag ; Vmin节电芯MFCL模块特征点2 Bit6：Vmax cell MFCL Point3 flag ; Vmax节电芯MFCL模块特征点3 Bit7：Vmin cell MFCL Point3 flag ; Vmin节电芯MFCL模块特征点3 | Rack | SOXdebug | RBMS_SOXdebugData2