## RX CAN-A
Node | Broadcast | comment | byte0 | byte1 | byte2 | byte3 | byte4 | byte5 | byte6 | byte7
N/A | 0x18000080 | OTA upgrade request
0x1827ddss | 0x1827FFss | PcCommand | TraceNumDownSample | Select | Dcmd_Pcmd (hi) | Dcmd_Pcmd (lo) kW | Qcmd (hi) | Qcmd (lo) kVAr | S0 (hi) bits | S0 (lo) bits
0x1803ddss | N/A | Save serial number | g_u16SNWords[]
0x1806ddss | 0x1806FFss | MCU restart/query | 0 restart / 1 ver. query
0x1807ddss | 0x1807FFss | OTA enable | 0 enable 0x1800 mailbox / 1 disable 0x1800 mailbox
0x0001ddss | 0x0001FFss | CAN ID assignment | CAN ID [0x02-0x09] / 0xAA force reset |  | config complete (0/1)
0x1810ddss | 0x1810FFss | Measurement poll | (triggers 21-msg burst)
0x1811ddss | 0x1811FFss | Configuration poll | (triggers config reply)
0x1826ddss | 0x1826FFss | PQ command | P preset % |  | Q preset % |  | Ibat ref |  | Vbat ref
N/A | 0x17FFFF00 | Broadcast P command | P% CANID 0x02 (int8) | P% CANID 0x03 | P% CANID 0x04 | P% CANID 0x05 | P% CANID 0x06 | P% CANID 0x07 | P% CANID 0x08 | P% CANID 0x09
N/A | 0x17FDFF00 | Broadcast Q command | Q% CANID 0x02 (int8) | Q% CANID 0x03 | Q% CANID 0x04 | Q% CANID 0x05 | Q% CANID 0x06 | Q% CANID 0x07 | Q% CANID 0x08 | Q% CANID 0x09
0x1830ddss | 0x1830FFss | Config param (0x1830) | g_sBodeCfg.f32FMax |  | Cal.Rirvac |  | FreqOffsetComp_temp |  | vGridLLGaincomp
0x1831ddss | 0x1831FFss | Config param (0x1831) | g_sBodeCfg.f32Mag |  | g_sBodeCfg.f32TAvg |  | g_sBodeCfg.u16PDec |  | g_sBodeCfg.f32FMin
0x1832ddss | 0x1832FFss | Config param (0x1832) | g_s16InternalDerateStart
0x1833ddss | 0x1833FFss | Config param (0x1833) | PCC_REFERENCE_VOLTAGE |  | GRID_RATED_FREQUENCY |  | FRE_WATT_ENABLE |  | VOLT_WATT_ENABLE
0x1834ddss | 0x1834FFss | Config param (0x1834) | VOLT_VAR_VREF_AUTO_ADJ_ENABLE |  | ANTI_ISLANDING_ENABLE |  | LIMIT_ACTIVE_POWER_ENABLE |  | REACTIVE_POWER_REG_MODE
0x1835ddss | 0x1835FFss | Config param (0x1835) | CHARGE_MODE |  | LIMIT_APPARENT_POWER_ENABLE
0x1836ddss | 0x1836FFss | Config param (0x1836) | OF_LEVEL1_PROTECTION_VALUE |  | UF_LEVEL1_PROTECTION_VALUE |  | OV_LEVEL1_PROTECTION_VALUE |  | UV_LEVEL1_PROTECTION_VALUE
0x1837ddss | 0x1837FFss | Config param (0x1837) | OF_LEVEL1_PROTECTION_TIME |  | UF_LEVEL1_PROTECTION_TIME |  | OV_LEVEL1_PROTECTION_TIME |  | UV_LEVEL1_PROTECTION_TIME
0x1838ddss | 0x1838FFss | Config param (0x1838) | OF_LEVEL1_PROTECTION_TIME (ms) |  | UF_LEVEL1_PROTECTION_TIME (ms) |  | OV_LEVEL1_PROTECTION_TIME (ms) |  | UV_LEVEL1_PROTECTION_TIME (ms)
0x1839ddss | 0x1839FFss | Config param (0x1839) | OF_LEVEL2_PROTECTION_VALUE |  | UF_LEVEL2_PROTECTION_VALUE |  | OV_LEVEL2_PROTECTION_VALUE |  | UV_LEVEL2_PROTECTION_VALUE
0x183Addss | 0x183AFFss | Config param (0x183A) | OF_LEVEL2_PROTECTION_TIME |  | UF_LEVEL2_PROTECTION_TIME |  | OV_LEVEL2_PROTECTION_TIME |  | UV_LEVEL2_PROTECTION_TIME
0x183Bddss | 0x183BFFss | Config param (0x183B) | OF_LEVEL2_PROTECTION_TIME (ms) |  | UF_LEVEL2_PROTECTION_TIME (ms) |  | OV_LEVEL2_PROTECTION_TIME (ms) |  | UV_LEVEL2_PROTECTION_TIME (ms)
0x183Cddss | 0x183CFFss | Config param (0x183C) | BATTERY_VOLTAGE_UPPER_LIMIT |  | BATTERY_VOLTAGE_LOWER_LIMIT
0x183Dddss | 0x183DFFss | Config param (0x183D) | ES_RAMP_RATE |  | ES_DELAY |  | ES_FREQUENCY_LOW |  | ES_FREQUENCY_HIGH
0x183Eddss | 0x183EFFss | Config param (0x183E) | ES_VOLTAGE_LOW |  | ES_VOLTAGE_HIGH |  | VOLT_VAR_TRESP |  | VARREF_TRESP
0x183Fddss | 0x183FFFss | Config param (0x183F) | FRE_WATT_TRESP |  | VOLT_WATT_TRESP |  | VOLT_VAR_VREF_AUTO_ADJ_TIME |  | LIMITED_POWER_PERCENTAGE
0x1840ddss | 0x1840FFss | Config param (0x1840) | FRE_WATT_KUF |  | FRE_WATT_DBOF |  | FRE_WATT_KOF |  | FRE_WATT_DBUF
0x1841ddss | 0x1841FFss | Config param (0x1841) | VOLT_WATT_V1 |  | VOLT_WATT_V2 |  | VOLT_WATT_P2 |  | VOLT_VAR_VREF
0x1842ddss | 0x1842FFss | Config param (0x1842) | VOLT_VAR_V1 |  | VOLT_VAR_V2 |  | VOLT_VAR_V3 |  | VOLT_VAR_V4
0x1843ddss | 0x1843FFss | Config param (0x1843) | VOLT_VAR_Q1 |  | VOLT_VAR_Q2 |  | VOLT_VAR_Q3 |  | VOLT_VAR_Q4
0x1844ddss | 0x1844FFss | Config param (0x1844) | WATT_VAR_P3P |  | WATT_VAR_P2P |  | WATT_VAR_P1P |  | WATT_VAR_P1
0x1845ddss | 0x1845FFss | Config param (0x1845) | WATT_VAR_Q3P |  | WATT_VAR_Q2P |  | WATT_VAR_Q1P |  | WATT_VAR_Q1
0x1846ddss | 0x1846FFss | Config param (0x1846) | WATT_VAR_P2 |  | WATT_VAR_P3 |  | ACTIVE_POWER_RISE_SPEED |  | CONST_POWER_FACTOR_EXCITATION
0x1847ddss | 0x1847FFss | Config param (0x1847) | WATT_VAR_Q2 |  | WATT_VAR_Q3 |  | REACTIVE_POWER_RISE_SPEED |  | CONST_POWER_FACTOR_SETTING
0x1848ddss | 0x1848FFss | Config param (0x1848) | ISLANDING_VOLTAGE_SLOPE |  | APPARENT_POWER_PERCENTAGE
- All messages are using Big-Endian
- Red is command messages
- Yellow is service and request messages
- Green is configuration messages
Config variable default, factor and range
Node | variable | default | factor | min | max | unit
0x1830 | g_sBodeCfg.f32FMax | 1000.0 | 0.1 | 0.1 | 1000.0 | Hz
| Cal.Rirvac | 3.0 | 0.1 | 0.0 | 10.0 | Ohm
| FreqOffsetComp_temp | 0.0 | 0.001 | -1.0 | 1.0 | Hz
| vGridLLGaincomp | 0.0 | 0.0001 | -0.002 | 0.002 | V
0x1831 | g_sBodeCfg.f32Mag | 1.0 | 0.01 | 0.0 | 300.0
| g_sBodeCfg.f32TAvg | 1.0 | 0.01 | 0.01 | 60.0 | Sec
| g_sBodeCfg.u16PDec | 50 | 1 | 5 | 50 | pts/Dec
| g_sBodeCfg.f32FMin | 1.0 | 0.1 | 0.1 | 1000.0 | Hz
0x1832 | g_s16InternalDerateStart | 60 | 1 | 40 | 90 | degC
0x1833 | PCC_REFERENCE_VOLTAGE | 690.0 | 1 | 680 | 730 | V
| GRID_RATED_FREQUENCY | 60 | 1 | 50 | 60 | Hz
| FRE_WATT_ENABLE | 1 | 1 | 0 | 1
| VOLT_WATT_ENABLE | 1 | 1 | 0 | 1
0x1834 | VOLT_VAR_VREF_AUTO_ADJ_ENABLE | 0 | 1 | 0 | 1
| ANTI_ISLANDING_ENABLE | 0 | 1 | 0 | 1
| LIMIT_ACTIVE_POWER_ENABLE | 1 | 1 | 0 | 1
| REACTIVE_POWER_REG_MODE | 0 | 1 | 0 | 3
0x1835 | CHARGE_MODE | 3 | 1 | 1 | 3
| LIMIT_APPARENT_POWER_ENABLE | 0 | 1 | 0 | 1
0x1836 | OF_LEVEL1_PROTECTION_VALUE | 61.2 | 0.01 | GRID_RATED_FREQUENCY+1.0 | GRID_RATED_FREQUENCY+6.0 | Hz
| UF_LEVEL1_PROTECTION_VALUE | 58.5 | 0.01 | GRID_RATED_FREQUENCY-10.0 | GRID_RATED_FREQUENCY-1.0 | Hz
| OV_LEVEL1_PROTECTION_VALUE | 1.10 | 0.01 | 1.1 | 1.2 | p.u.
| UV_LEVEL1_PROTECTION_VALUE | 0.88 | 0.01 | 0.0 | 0.88 | p.u.
0x1837 | OF_LEVEL1_PROTECTION_TIME | 300000 | 1 | 180.0 | 1000.0 | Sec
| UF_LEVEL1_PROTECTION_TIME | 300000 | 1 | 180.0 | 1000.0 | Sec
| OV_LEVEL1_PROTECTION_TIME | 13000 | 1 | 1.0 | 13.0 | Sec
| UV_LEVEL1_PROTECTION_TIME | 21000 | 1 | 2.0 | 50.0 | Sec
0x1838 | OF_LEVEL1_PROTECTION_TIME (ms) | 300000 | 1 | 180000 | 1000000 | mSec
| UF_LEVEL1_PROTECTION_TIME (ms) | 300000 | 1 | 180000 | 1000000 | mSec
| OV_LEVEL1_PROTECTION_TIME (ms) | 13000 | 1 | 1000 | 13000 | mSec
| UV_LEVEL1_PROTECTION_TIME (ms) | 21000 | 1 | 2000 | 50000 | mSec
0x1839 | OF_LEVEL2_PROTECTION_VALUE | 62.0 | 0.01 | GRID_RATED_FREQUENCY+1.8 | GRID_RATED_FREQUENCY+6.0 | Hz
| UF_LEVEL2_PROTECTION_VALUE | 56.5 | 0.01 | GRID_RATED_FREQUENCY-10.0 | GRID_RATED_FREQUENCY-3.0 | Hz
| OV_LEVEL2_PROTECTION_VALUE | 1.20 | 0.01 | 1.2 | 1.2 | p.u.
| UV_LEVEL2_PROTECTION_VALUE | 0.5 | 0.01 | 0.0 | 0.5 | p.u.
0x183A | OF_LEVEL2_PROTECTION_TIME | 160 | 1 | 0.16 | 1000.0 | Sec
| UF_LEVEL2_PROTECTION_TIME | 160 | 1 | 0.16 | 1000.0 | Sec
| OV_LEVEL2_PROTECTION_TIME | 160 | 1 | 0.16 | 0.16 | Sec
| UV_LEVEL2_PROTECTION_TIME | 2000 | 1 | 0.16 | 21.0 | Sec
0x183B | OF_LEVEL2_PROTECTION_TIME (ms) | 160 | 1 | 160 | 1000000 | mSec
| UF_LEVEL2_PROTECTION_TIME (ms) | 160 | 1 | 160 | 1000000 | mSec
| OV_LEVEL2_PROTECTION_TIME (ms) | 160 | 1 | 160 | 160 | mSec
| UV_LEVEL2_PROTECTION_TIME (ms) | 2000 | 1 | 160 | 21000 | mSec
0x183C | BATTERY_VOLTAGE_UPPER_LIMIT | 1518.0 | 1 | 1200 | 1570 | V
| BATTERY_VOLTAGE_LOWER_LIMIT | 1000.0 | 1 | 900 | 1200 | V
0x183D | ES_RAMP_RATE | 300.0 | 0.1 | 1.0 | 1000.0 | Sec
| ES_DELAY | 300.0 | 0.1 | 0.0 | 600.0 | Sec
| ES_FREQUENCY_LOW | 59.5 | 0.01 | GRID_RATED_FREQUENCY-1.0 | GRID_RATED_FREQUENCY-0.1 | Hz
| ES_FREQUENCY_HIGH | 60.1 | 0.01 | GRID_RATED_FREQUENCY+0.1 | GRID_RATED_FREQUENCY+1.0 | Hz
0x183E | ES_VOLTAGE_LOW | 0.917 | 0.001 | 0.88 | 0.95 | p.u.
| ES_VOLTAGE_HIGH | 1.05 | 0.001 | 1.05 | 1.06 | p.u.
| VOLT_VAR_TRESP | 5.0 | 0.01 | 1.0 | 90.0 | Sec
| VARREF_TRESP | 5.0 | 0.1 | 0.1 | 10.0 | Sec
0x183F | FRE_WATT_TRESP | 5.0 | 0.01 | 0.2 | 10.0 | Sec
| VOLT_WATT_TRESP | 10.0 | 0.01 | 0.5 | 60.0 | Sec
| VOLT_VAR_VREF_AUTO_ADJ_TIME | 300.0 | 1 | 300.0 | 5000.0 | Sec
| LIMITED_POWER_PERCENTAGE | 100.0 | 1 | 0 | 110 | %
0x1840 | FRE_WATT_KUF | 0.05 | 0.001 | 0.02 | 0.05 | p.u.
| FRE_WATT_DBOF | 0.036 | 0.001 | 0.017 | 1.0 | Hz
| FRE_WATT_KOF | 0.05 | 0.001 | 0.02 | 0.05 | p.u.
| FRE_WATT_DBUF | 0.036 | 0.001 | 0.017 | 1.0 | Hz
0x1841 | VOLT_WATT_V1 | 1.06 | 0.001 | 1.05 | 1.09 | p.u.
| VOLT_WATT_V2 | 1.1 | 0.001 | VOLT_WATT_V1+0.01 | 1.1 | p.u.
| VOLT_WATT_P2 | -1.0 | 0.001 | -1.0 | 1.0 | p.u.
| VOLT_VAR_VREF | 1.0 | 0.001 | 0.95 | 1.05 | p.u.
0x1842 | VOLT_VAR_V1 | 0.92 | 0.001 | VOLT_VAR_VREF-0.18 | VOLT_VAR_V2-0.02 | p.u.
| VOLT_VAR_V2 | 0.98 | 0.001 | VOLT_VAR_VREF-0.03 | VOLT_VAR_VREF | p.u.
| VOLT_VAR_V3 | 1.02 | 0.001 | VOLT_VAR_VREF | VOLT_VAR_VREF+0.03 | p.u.
| VOLT_VAR_V4 | 1.08 | 0.001 | VOLT_VAR_V3+0.02 | VOLT_VAR_VREF+0.18 | p.u.
0x1843 | VOLT_VAR_Q1 | 0.44 | 0.001 | 0.0 | 1.0 | p.u.
| VOLT_VAR_Q2 | 0.0 | 0.001 | -1.0 | 1.0 | p.u.
| VOLT_VAR_Q3 | 0.0 | 0.001 | -1.0 | 1.0 | p.u.
| VOLT_VAR_Q4 | -0.44 | 0.001 | -1.0 | 0.0 | p.u.
0x1844 | WATT_VAR_P3P | -1.0 | 0.01 | -1.0 | WATT_VAR_P2P-0.1 | p.u.
| WATT_VAR_P2P | -0.5 | 0.01 | -0.8 | -0.4 | p.u.
| WATT_VAR_P1P | -0.2 | 0.01 | WATT_VAR_P2P+0.1 | 0.0 | p.u.
| WATT_VAR_P1 | 0.2 | 0.01 | 0.0 | WATT_VAR_P2-0.1 | p.u.
0x1845 | WATT_VAR_Q3P | 0.44 | 0.01 | -1.0 | 1.0 | p.u.
| WATT_VAR_Q2P | 0.0 | 0.01 | -1.0 | 1.0 | p.u.
| WATT_VAR_Q1P | 0.0 | 0.01 | -1.0 | 1.0 | p.u.
| WATT_VAR_Q1 | 0.0 | 0.01 | -1.0 | 1.0 | p.u.
0x1846 | WATT_VAR_P2 | 0.5 | 0.01 | 0.4 | 0.8 | p.u.
| WATT_VAR_P3 | 1.0 | 0.01 | WATT_VAR_P2+0.1 | 1.0 | p.u.
| ACTIVE_POWER_RISE_SPEED | 10000 | 1 | 100 | 10000 | kW/sec
| CONST_POWER_FACTOR_EXCITATION | 0 | 1 | 0 | 1
0x1847 | WATT_VAR_Q2 | 0.0 | 0.01 | -1.0 | 1.0 | p.u.
| WATT_VAR_Q3 | -0.44 | 0.01 | -1.0 | 1.0 | p.u.
| REACTIVE_POWER_RISE_SPEED | 10000 | 1 | 100 | 10000 | kVar/sec
| CONST_POWER_FACTOR_SETTING | 1.0 | 0.01 | 0.0 | 1.0
0x1848 | ISLANDING_VOLTAGE_SLOPE | 100.0 | 1 | 10 | 200 | V/sec
| APPARENT_POWER_PERCENTAGE | 100.0 | 1 | 0 | 100 | %
Command variable default, factor and range
Node | name | variable | default | factor | min | max | unit
0x1826ssdd | P preset % | ACTIVE_POWER_PRESET | 0 | 0.01 | -115.0 | 115.0 | %
| Q preset % | REACTIVE_POWER_PRESET | 0 | 0.01 | -115.0 | 115.0 | %
| Ibat ref | IBAT_REF | 0 | 0.1 | -350.0 | 350.0 | A
| Vbat ref | VBAT_REF | 0 | 1 | 950 | 1520 | V
0x17FFFF00 | Broadcast P command | s16Percent | 0 | 1 | -115 | 115 | %
0x17FDFF00 | Braodcast Q command | s16Percent | 0 | 1 | -115 | 115 | %

## TX CAN-A
Node | Comment | byte0 | byte1 | byte2 | byte3 | byte4 | byte5 | byte6 | byte7
0x18000088 | OTA upgrade ready reply | 0x41 | 0x02 | flashCanId | 0x01 | canRecvMode
0x1A02ssdd | reply CAN ID assignment to SCU | 0 | ota enable status | 0 | 0 | 0 | GPIO63(0 or 1) | 0 | 0
0x1AA1ssdd | reply CAN ID assignment to PMS | 0 | ota enable status | 0 | 0 | 0 | GPIO63(0 or 1) | 0 | 0
0x1A03ssdd | reply serial number saving | SN word0 (hi) | SN word0 (lo) | SN word1 (hi) | SN word1 (lo) | SN word2 (hi) | SN word2 (lo) | SN word3 (hi) | SN word3 (lo)
0x1A06ssdd | reply MCU restart/query | git hash (hi) | git hash | git hash | git hash (lo) | CPU1 major ver | CPU1 minor ver | CPLD major | CPLD minor
0x1A07ssdd | reply OTA enable | mailbox status / 1=enabled / 0=disabled
0x1A27ssdd | reply PcCommand echo-back | g_PcCommand.S3 hi | S3 lo | S2 hi | S2 lo | S1 hi | S1 lo | S0 hi | S0 lo
0x1A26ssdd | reply PQ command (0x1826) | P preset % |  | Q preset % |  | Ibat ref |  | Vbat ref
0x1AFFssdd | reply broadcast P cmd (0x17FF) | P% CANID 0x02 | P% CANID 0x03 | P% CANID 0x04 | P% CANID 0x05 | P% CANID 0x06 | P% CANID 0x07 | P% CANID 0x08 | P% CANID 0x09
0x1AFDssdd | reply broadcast Q cmd (0x17FD) | Q% CANID 0x02 | Q% CANID 0x03 | Q% CANID 0x04 | Q% CANID 0x05 | Q% CANID 0x06 | Q% CANID 0x07 | Q% CANID 0x08 | Q% CANID 0x09
0x1A80ssdd | Battery & power | Ibat |  | Vbat |  | Pavg10cyc (kW) |  | Qavg10cyc (kVAr)
0x1A81ssdd | IGBT temps W,V | TempIGBT_W1 |  | TempIGBT_W2 |  | TempIGBT_V1 |  | TempIGBT_V2
0x1A82ssdd | IGBT temps U, DC bus, int filter | TempIGBT_U1 |  | TempIGBT_U2 |  | TempDcBusBrd |  | TempIntFiltBrd
0x1A83ssdd | Clock since reset | days |  | hours |  | minutes |  | seconds
0x1A84ssdd | Temps, ROCOF, FreqAvg | TempHsInAir |  | TempCplateIn |  | ROCOF |  | FreqAvg
0x1A85ssdd | Freq trip elapsed | OF1Elapsed |  | UF1Elapsed |  | OF2Elapsed |  | UF2Elapsed
0x1A86ssdd | Avg line V & per-phase p.u. | AvgVll |  | VllC p.u. |  | VllA p.u. |  | VllB p.u.
0x1A87ssdd | Voltage trip elapsed | OV1Elapsed |  | UV1Elapsed |  | OV2Elapsed |  | UV2Elapsed
0x1A88ssdd | DC bus & grid phase currents | VdcTop |  | VdcBot |  | IgridA |  | IgridB
0x1A89ssdd | IEEE flags | configFlag |  | C2flag |  | Local1547Flag |  | C2State
0x1A8Assdd | IgridC & exec-time counters | IgridC |  | ExecUsecMax |  | BgExecUsecMax |  | Cpu2ExecUsecMax
0x1A8Bssdd | Vref DQ & PQ ref | VrefD |  | VrefQ |  | Pref (kW) |  | Qref (kVAr)
0x1A8Cssdd | Current ref & voltage cmd | Iref D |  | Iref Q |  | Vcmd D |  | Vcmd Q
0x1A8Dssdd | PWM sync, C2 state elapsed | PwmSyncMinMs |  | C2CurrStElapsed |  | C2PrevStElapsed |  | PrevPCSState
0x1A8Essdd | Anti-island + VoltVar Vref | AIDeltaIdMax |  | AIDeltaIqMax |  | AISatCntMax |  | VoltVar VrefPU
0x1A8Fssdd | Vdq out & Idq feedback | VdqFdbk D |  | VdqFdbk Q |  | IdqFdbk D |  | IdqFdbk Q
0x1A90ssdd | FreqWatt / VoltWatt droop | FreqWatt DPpu |  | FreqWatt fpreHz |  | FreqWatt PprePU |  | VoltWatt DPpu
0x1A91ssdd | Pavl / thermal / mod index | PavlGeneratePU |  | PavlAbsorbPU |  | ThermalDerateFactor |  | Modulation index
0x1A92ssdd | Fault words | Fault Short0 |  | Fault Short1 |  | Fault Short2 |  | Fault Short3
0x1A93ssdd | PCS state, discrete, CPU2 state | PCSState |  | DiscreteInputs S0 |  | C2State |  | (unused)
0x1A94ssdd | P/Q envelope after curtailment | PmaxPU |  | PminPU |  | QmaxPU |  | QminPU
0x1A95ssdd | Vdc max & IinvMax A/B | VdcTopMax |  | VdcBotMax |  | IinvMaxA |  | IinvMaxB
0x1A9Dssdd | IinvMaxC & VinvMax phases | IinvMaxC |  | VinvMaxA |  | VinvMaxB |  | VinvMaxC
0x1A9Essdd | Per-phase active power + IbatMax | Pa (kW) |  | Pb (kW) |  | Pc (kW) |  | IbatMax (A)
0x1A9Fssdd | Per-phase reactive power + Pdc | Qa (kVAr) |  | Qb (kVAr) |  | Qc (kVAr) |  | Pdc (kW)
0x1AA0ssdd | Per-phase power factor + recent fault info | pfa |  | pfb |  | pfc |  | RecentRecordIdx×10 + SnapshotCount (0; 11..43)
0x1AA1ssdd | ADC offset cal + Rinsul | IinvOffsetMaxAbs |  | IgridOffsetMaxAbs |  | IdcOffsetSum |  | Rinsul (kOhm)
0x1A96ssdd | trace_buffer1 | iInvU |  | iInvV |  | iInvW |  | iNPmod
0x1A97ssdd | trace_buffer2 | iGridU |  | iGridV |  | iGridW |  | iBat
0x1A98ssdd | trace_buffer3 | vBusPos |  | vBusNeg |  | VcmdDQ.D |  | VcmdDQ.Q
0x1A99ssdd | trace_buffer4 | DabcOrig.A |  | DabcOrig.B |  | DabcOrig.C |  | ThetaPLL
0x1A9Assdd | trace_buffer5 | Icmd.D |  | Icmd.Q |  | IacRegErr.D |  | IacRegErr.Q
0x1A9Bssdd | trace_buffer6 | VgridLN.A |  | VgridLN.B |  | VgridLN.C |  | VgridMagPLL
0x1A9Cssdd | Bode sweep header | 0xB0DE magic |  | u16PointCount |  | log10(fMin) x1000 |  | log10(fMax) x1000
0x1A9Cssdd | Bode sweep point | log10(freq) x1000 |  | gain_dB x10 |  | phase_deg x10 |  | pointIndex
0x1A30ssdd | Reply config (0x1A30) | g_sBodeCfg.f32FMax |  | Cal.Rirvac |  | FreqOffsetComp_temp |  | vGridLLGaincomp
0x1A31ssdd | Reply config (0x1A31) | g_sBodeCfg.f32Mag |  | g_sBodeCfg.f32TAvg |  | g_sBodeCfg.u16PDec |  | g_sBodeCfg.f32FMin
0x1A32ssdd | Reply config (0x1A32) | g_s16InternalDerateStart
0x1A33ssdd | Reply config (0x1A33) | PCC_REFERENCE_VOLTAGE |  | GRID_RATED_FREQUENCY |  | FRE_WATT_ENABLE |  | VOLT_WATT_ENABLE
0x1A34ssdd | Reply config (0x1A34) | VOLT_VAR_VREF_AUTO_ADJ_ENABLE |  | ANTI_ISLANDING_ENABLE |  | LIMIT_ACTIVE_POWER_ENABLE |  | REACTIVE_POWER_REG_MODE
0x1A35ssdd | Reply config (0x1A35) | CHARGE_MODE |  | LIMIT_APPARENT_POWER_ENABLE
0x1A36ssdd | Reply config (0x1A36) | OF_LEVEL1_PROTECTION_VALUE |  | UF_LEVEL1_PROTECTION_VALUE |  | OV_LEVEL1_PROTECTION_VALUE |  | UV_LEVEL1_PROTECTION_VALUE
0x1A37ssdd | Reply config (0x1A37) | OF_LEVEL1_PROTECTION_TIME |  | UF_LEVEL1_PROTECTION_TIME |  | OV_LEVEL1_PROTECTION_TIME |  | UV_LEVEL1_PROTECTION_TIME
0x1A38ssdd | Reply config (0x1A38) | OF_LEVEL1_PROTECTION_TIME (ms) |  | UF_LEVEL1_PROTECTION_TIME (ms) |  | OV_LEVEL1_PROTECTION_TIME (ms) |  | UV_LEVEL1_PROTECTION_TIME (ms)
0x1A39ssdd | Reply config (0x1A39) | OF_LEVEL2_PROTECTION_VALUE |  | UF_LEVEL2_PROTECTION_VALUE |  | OV_LEVEL2_PROTECTION_VALUE |  | UV_LEVEL2_PROTECTION_VALUE
0x1A3Assdd | Reply config (0x1A3A) | OF_LEVEL2_PROTECTION_TIME |  | UF_LEVEL2_PROTECTION_TIME |  | OV_LEVEL2_PROTECTION_TIME |  | UV_LEVEL2_PROTECTION_TIME
0x1A3Bssdd | Reply config (0x1A3B) | OF_LEVEL2_PROTECTION_TIME (ms) |  | UF_LEVEL2_PROTECTION_TIME (ms) |  | OV_LEVEL2_PROTECTION_TIME (ms) |  | UV_LEVEL2_PROTECTION_TIME (ms)
0x1A3Cssdd | Reply config (0x1A3C) | BATTERY_VOLTAGE_UPPER_LIMIT |  | BATTERY_VOLTAGE_LOWER_LIMIT
0x1A3Dssdd | Reply config (0x1A3D) | ES_RAMP_RATE |  | ES_DELAY |  | ES_FREQUENCY_LOW |  | ES_FREQUENCY_HIGH
0x1A3Essdd | Reply config (0x1A3E) | ES_VOLTAGE_LOW |  | ES_VOLTAGE_HIGH |  | VOLT_VAR_TRESP |  | VARREF_TRESP
0x1A3Fssdd | Reply config (0x1A3F) | FRE_WATT_TRESP |  | VOLT_WATT_TRESP |  | VOLT_VAR_VREF_AUTO_ADJ_TIME |  | LIMITED_POWER_PERCENTAGE
0x1A40ssdd | Reply config (0x1A40) | FRE_WATT_KUF |  | FRE_WATT_DBOF |  | FRE_WATT_KOF |  | FRE_WATT_DBUF
0x1A41ssdd | Reply config (0x1A41) | VOLT_WATT_V1 |  | VOLT_WATT_V2 |  | VOLT_WATT_P2 |  | VOLT_VAR_VREF
0x1A42ssdd | Reply config (0x1A42) | VOLT_VAR_V1 |  | VOLT_VAR_V2 |  | VOLT_VAR_V3 |  | VOLT_VAR_V4
0x1A43ssdd | Reply config (0x1A43) | VOLT_VAR_Q1 |  | VOLT_VAR_Q2 |  | VOLT_VAR_Q3 |  | VOLT_VAR_Q4
0x1A44ssdd | Reply config (0x1A44) | WATT_VAR_P3P |  | WATT_VAR_P2P |  | WATT_VAR_P1P |  | WATT_VAR_P1
0x1A45ssdd | Reply config (0x1A45) | WATT_VAR_Q3P |  | WATT_VAR_Q2P |  | WATT_VAR_Q1P |  | WATT_VAR_Q1
0x1A46ssdd | Reply config (0x1A46) | WATT_VAR_P2 |  | WATT_VAR_P3 |  | ACTIVE_POWER_RISE_SPEED |  | CONST_POWER_FACTOR_EXCITATION
0x1A47ssdd | Reply config (0x1A47) | WATT_VAR_Q2 |  | WATT_VAR_Q3 |  | REACTIVE_POWER_RISE_SPEED |  | CONST_POWER_FACTOR_SETTING
0x1A48ssdd | Reply config (0x1A48) | ISLANDING_VOLTAGE_SLOPE |  | APPARENT_POWER_PERCENTAGE
- All messages are using Big-Endian
- Red is command response messages
- Yellow is service and request response messages
- Green is configuration response messages
- Blue is measurement polling response messages (measurement burst) and debug trace reporting messages
Measurement variable default, factor and range
Node | name | variable | default | factor | min | max | unit
0x1A80ssdd | Ibat | IbatFilt | 0 | 0.125 | -4096 | 4096 | A
| Vbat | VbatFilt | 0 | 0.125 | -4096 | 4096 | V
| Pavg10cyc (kW) | f32Pavg10cyc | 0 | 0.125 | -4096 | 4096 | kW
| Qavg10cyc (kVAr) | f32Qavg10cyc | 0 | 0.125 | -4096 | 4096 | kVAr
0x1A81ssdd | TempIGBT_W1 | g_sTemperature[TempIGBT_W1] | 0 | 0.125 | -4096 | 4096 | degC
| TempIGBT_W2 | g_sTemperature[TempIGBT_W2] | 0 | 0.125 | -4096 | 4096 | degC
| TempIGBT_V1 | g_sTemperature[TempIGBT_V1] | 0 | 0.125 | -4096 | 4096 | degC
| TempIGBT_V2 | g_sTemperature[TempIGBT_V2] | 0 | 0.125 | -4096 | 4096 | degC
0x1A82ssdd | TempIGBT_U1 | g_sTemperature[TempIGBT_U1] | 0 | 0.125 | -4096 | 4096 | degC
| TempIGBT_U2 | g_sTemperature[TempIGBT_U2] | 0 | 0.125 | -4096 | 4096 | degC
| TempDcBusBrd | g_sTemperature[TempDcBusBrd] | 0 | 0.125 | -4096 | 4096 | degC
| TempIntFiltBrd | g_sTemperature[TempIntFiltBrd] | 0 | 0.125 | -4096 | 4096 | degC
0x1A83ssdd | days | g_ClockSinceReset.day | 0 | 0.125 | -4096 | 4096 | day
| hours | g_ClockSinceReset.hour | 0 | 0.125 | -4096 | 4096 | hr
| minutes | g_ClockSinceReset.minute | 0 | 0.125 | -4096 | 4096 | min
| seconds | g_ClockSinceReset.second | 0 | 0.125 | -4096 | 4096 | sec
0x1A84ssdd | TempHsInAir | g_sTemperature[TempHsInAir] | 0 | 0.125 | -4096 | 4096 | degC
| TempCplateIn | g_sTemperature[TempColdPltInWtr] | 0 | 0.125 | -4096 | 4096 | degC
| ROCOF (Hz/s) | sIEEE1547.f32ROCOF | 0 | 0.01 | -327.68 | 327.67 | Hz/s
| FreqAvg (Hz) | f32FreqAvg60cyc | 0 | 0.01 | -327.68 | 327.67 | Hz
0x1A85ssdd | OF1Elapsed (s) | sFreqTrip.f32ElapsedSecOF1 | 0 | 0.1 | -3276.8 | 3276.7 | sec
| UF1Elapsed (s) | sFreqTrip.f32ElapsedSecUF1 | 0 | 0.1 | -3276.8 | 3276.7 | sec
| OF2Elapsed (s) | sFreqTrip.f32ElapsedSecOF2 | 0 | 0.1 | -3276.8 | 3276.7 | sec
| UF2Elapsed (s) | sFreqTrip.f32ElapsedSecUF2 | 0 | 0.1 | -3276.8 | 3276.7 | sec
0x1A86ssdd | AvgVll (V) | avg(VLLrms10cyc A,B,C) | 0 | 0.1 | -3276.8 | 3276.7 | V
| VllC (p.u.) | VLLrms10cyc.f32C | 0 | 0.01 | -327.68 | 327.67 | p.u.
| VllA (p.u.) | VLLrms10cyc.f32A | 0 | 0.01 | -327.68 | 327.67 | p.u.
| VllB (p.u.) | VLLrms10cyc.f32B | 0 | 0.01 | -327.68 | 327.67 | p.u.
0x1A87ssdd | OV1Elapsed (s) | sVoltTrip.f32ElapsedSecOV1 | 0 | 0.1 | -3276.8 | 3276.7 | sec
| UV1Elapsed (s) | sVoltTrip.f32ElapsedSecUV1 | 0 | 0.1 | -3276.8 | 3276.7 | sec
| OV2Elapsed (s) | sVoltTrip.f32ElapsedSecOV2 | 0 | 0.1 | -3276.8 | 3276.7 | sec
| UV2Elapsed (s) | sVoltTrip.f32ElapsedSecUV2 | 0 | 0.1 | -3276.8 | 3276.7 | sec
0x1A88ssdd | VdcTop (V) | VdcTopFilt | 0 | 0.1 | -3276.8 | 3276.7 | V
| VdcBot (V) | VdcBotFilt | 0 | 0.1 | -3276.8 | 3276.7 | V
| IgridA (A) | Igridrms.f32A | 0 | 0.1 | -3276.8 | 3276.7 | A
| IgridB (A) | Igridrms.f32B | 0 | 0.1 | -3276.8 | 3276.7 | A
0x1A89ssdd | configFlag | sIEEE1547.configFlag.All | 0 | 1 | 0 | 65535
| C2flag | sIEEE1547.flag.All | 0 | 1 | 0 | 65535
| Local1547Flag | BuildLocal1547Flag() packed uint16 | 0 | 1 | 0 | 65535
| C2State | g_sIPCDataIn.C2State | 0 | 1 | 0 | 65535
0x1A8Assdd | IgridC (A) | Igridrms.f32C | 0 | 0.1 | -3276.8 | 3276.7 | A
| ExecUsecMax (us) | f32ExecUsecMax | 0 | 1 | -32768 | 32767 | us
| BgExecUsecMax (us) | g_f32BgExecUsecMax | 0 | 1 | -32768 | 32767 | us
| Cpu2ExecUsecMax (us) | f32Cpu2ExecUsecMax | 0 | 1 | -32768 | 32767 | us
0x1A8Bssdd | VrefD (V) | VrefDQ.f32D | 0 | 1 | -32768 | 32767 | V
| VrefQ (V) | VrefDQ.f32Q | 0 | 1 | -32768 | 32767 | V
| Pref (kW) | PQref.f32P | 0 | 1 | -32768 | 32767 | kW
| Qref (kVAr) | PQref.f32Q | 0 | 1 | -32768 | 32767 | kVAr
0x1A8Cssdd | Iref D (A) | Iref.f32D | 0 | 1 | -32768 | 32767 | A
| Iref Q (A) | Iref.f32Q | 0 | 1 | -32768 | 32767 | A
| Vcmd D (V) | VcmdDQ.f32D | 0 | 1 | -32768 | 32767 | V
| Vcmd Q (V) | VcmdDQ.f32Q | 0 | 1 | -32768 | 32767 | V
0x1A8Dssdd | PwmSyncMinMs (ms) | g_f32PwmSyncMinPeriodMs | 0 | 0.001 | -32.768 | 32.767 | ms
| C2CurrStElapsed (s) | sIEEE1547.f32CurrentStElapsedSec | 0 | 1 | -32768 | 32767 | sec
| C2PrevStElapsed (s) | sIEEE1547.f32PrevStElapsedSec | 0 | 1 | -32768 | 32767 | sec
| PrevPCSState | g_ePrevPCSState | 0 | 0.125 | -4096 | 4096
0x1A8Essdd | AIDeltaIdMax (A) | g_f32AIDeltaIdMax | 0 | 0.1 | -3276.8 | 3276.7 | A
| AIDeltaIqMax (A) | g_f32AIDeltaIqMax | 0 | 0.1 | -3276.8 | 3276.7 | A
| AISatCntMax | g_u32AISatCounterMax | 0 | 1 | -32768 | 32767
| VoltVar VrefPU (p.u.) | sIEEE1547.sVoltVar.f32VrefPU | 0 | 0.001 | -32.768 | 32.767 | p.u.
0x1A8Fssdd | VdqFdbk D (V) | VdqOutFdbk.f32D | 0 | 1 | -32768 | 32767 | V
| VdqFdbk Q (V) | VdqOutFdbk.f32Q | 0 | 1 | -32768 | 32767 | V
| IdqFdbk D (A) | IdqFdbk.f32D | 0 | 0.1 | -3276.8 | 3276.7 | A
| IdqFdbk Q (A) | IdqFdbk.f32Q | 0 | 0.1 | -3276.8 | 3276.7 | A
0x1A90ssdd | FreqWatt DPpu (p.u.) | sIEEE1547.sFreqWatt.f32DPpu | 0 | 0.01 | -327.68 | 327.67 | p.u.
| FreqWatt fpreHz (Hz) | sIEEE1547.sFreqWatt.f32fpreHz | 0 | 0.01 | -327.68 | 327.67 | Hz
| FreqWatt PprePU (p.u.) | sIEEE1547.sFreqWatt.f32PprePU | 0 | 0.001 | -32.768 | 32.767 | p.u.
| VoltWatt DPpu (p.u.) | sIEEE1547.sVoltWatt.f32DPpu | 0 | 0.01 | -327.68 | 327.67 | p.u.
0x1A91ssdd | PavlGeneratePU (p.u.) | sIEEE1547Config.PQCmdToCPU2.f32PavlGeneratePU | 0 | 0.001 | -32.768 | 32.767 | p.u.
| PavlAbsorbPU (p.u.) | sIEEE1547Config.PQCmdToCPU2.f32PavlAbsorbPU | 0 | 0.001 | -32.768 | 32.767 | p.u.
| ThermalDerateFactor (p.u.) | g_f32ThermalDerateFactor | 0 | 0.001 | -32.768 | 32.767 | p.u.
| Modulation index | ModIndex | 0 | 0.001 | -32.768 | 32.767
0x1A92ssdd | Fault Short0 (raw uint16) | g_sFault.Short.Short0 | 0 | 1 | 0 | 65535
| Fault Short1 (raw uint16) | g_sFault.Short.Short1 | 0 | 1 | 0 | 65535
| Fault Short2 (raw uint16) | g_sFault.Short.Short2 | 0 | 1 | 0 | 65535
| Fault Short3 (raw uint16) | g_sFault.Short.Short3 | 0 | 1 | 0 | 65535
0x1A93ssdd | PCSState | g_ePCSState | 0 | 1 | -32768 | 32767
| DiscreteInputs S0 | g_sDiscreteInputs.Short.S0 | 0 | 1 | -32768 | 32767
| C2State (raw uint16) | g_sIPCDataIn.C2State | 0 | 1 | 0 | 65535
| (unused) | 0 | 0 | 1 | 0 | 0
0x1A94ssdd | PmaxPU (p.u.) | sIEEE1547.f32PmaxPU | 0 | 0.001 | -32.768 | 32.767 | p.u.
| PminPU (p.u.) | sIEEE1547.f32PminPU | 0 | 0.001 | -32.768 | 32.767 | p.u.
| QmaxPU (p.u.) | sIEEE1547.f32QmaxPU | 0 | 0.001 | -32.768 | 32.767 | p.u.
| QminPU (p.u.) | sIEEE1547.f32QminPU | 0 | 0.001 | -32.768 | 32.767 | p.u.
0x1A95ssdd | VdcTopMax (V) | VdcTop_max | 0 | 0.1 | -3276.8 | 3276.7 | V
| VdcBotMax (V) | VdcBottom_max | 0 | 0.1 | -3276.8 | 3276.7 | V
| IinvMaxA (A) | IinvMax.f32A | 0 | 0.1 | -3276.8 | 3276.7 | A
| IinvMaxB (A) | IinvMax.f32B | 0 | 0.1 | -3276.8 | 3276.7 | A
0x1A9Dssdd | IinvMaxC (A) | IinvMax.f32C | 0 | 0.1 | -3276.8 | 3276.7 | A
| VinvMaxA (V) | VinvMax.f32A | 0 | 0.1 | -3276.8 | 3276.7 | V
| VinvMaxB (V) | VinvMax.f32B | 0 | 0.1 | -3276.8 | 3276.7 | V
| VinvMaxC (V) | VinvMax.f32C | 0 | 0.1 | -3276.8 | 3276.7 | V
0x1A9Essdd | Pa (kW) | g_sCla1Task2Out.f32Pa | 0 | 0.1 | -3276.8 | 3276.7 | kW
| Pb (kW) | g_sCla1Task2Out.f32Pb | 0 | 0.1 | -3276.8 | 3276.7 | kW
| Pc (kW) | g_sCla1Task2Out.f32Pc | 0 | 0.1 | -3276.8 | 3276.7 | kW
| IbatMax (A) | IbatMax | 0 | 1 | -32768 | 32767 | A
0x1A9Fssdd | Qa (kVAr) | g_sCla1Task2Out.f32Qa | 0 | 0.1 | -3276.8 | 3276.7 | kVAr
| Qb (kVAr) | g_sCla1Task2Out.f32Qb | 0 | 0.1 | -3276.8 | 3276.7 | kVAr
| Qc (kVAr) | g_sCla1Task2Out.f32Qc | 0 | 0.1 | -3276.8 | 3276.7 | kVAr
| Pdc (kW) | g_sCla1Task1Out.f32Pdc | 0 | 0.1 | -3276.8 | 3276.7 | kW
0x1AA0ssdd | pfa | g_sCla1Task2Out.f32pfa | 0 | 0.001 | -32.768 | 32.767
| pfb | g_sCla1Task2Out.f32pfb | 0 | 0.001 | -32.768 | 32.767
| pfc | g_sCla1Task2Out.f32pfc | 0 | 0.001 | -32.768 | 32.767
| RecentRecordIdx*10 + SnapCount | GetMostRecentRecordIdx()*10 + g_u16LastSavedSnapshotCount | 0 | 1 | 0 | 43
0x1AA1ssdd | IinvOffsetMaxAbs (A) | IinvOffsetMaxAbs | 0 | 0.01 | -327.68 | 327.67 | A
| IgridOffsetMaxAbs (A) | IgridOffsetMaxAbs | 0 | 0.01 | -327.68 | 327.67 | A
| IdcOffsetSum (A) | IdcOffsetSum | 0 | 0.01 | -327.68 | 327.67 | A
| Rinsul (kOhm) | Rinsul | 0 | 1 | -32768 | 32767 | kOhm
Debug trace variable default, factor and range
Node | name | variable | default | factor | min | max | unit
0x1A96ssdd | iInvU | AdcData[Ch_iInvU] | 0 | 0.1 | -3276.8 | 3276.7 | A
| iInvV | AdcData[Ch_iInvV] | 0 | 0.1 | -3276.8 | 3276.7 | A
| iInvW | AdcData[Ch_iInvW] | 0 | 0.1 | -3276.8 | 3276.7 | A
| iNPmod | g_sVmidInfo.f32iNPmod | 0 | 0.1 | -3276.8 | 3276.7 | A
0x1A97ssdd | iGridU | AdcData[Ch_iGridU] | 0 | 0.1 | -3276.8 | 3276.7 | A
| iGridV | AdcData[Ch_iGridV] | 0 | 0.1 | -3276.8 | 3276.7 | A
| iGridW | AdcData[Ch_iGridW] | 0 | 0.1 | -3276.8 | 3276.7 | A
| iBat | AdcData[Ch_iBat] | 0 | 0.1 | -3276.8 | 3276.7 | A
0x1A98ssdd | vBusPos | AdcData[Ch_vBusPos] | 0 | 0.1 | -3276.8 | 3276.7 | V
| vBusNeg | AdcData[Ch_vBusNeg] | 0 | 0.1 | -3276.8 | 3276.7 | V
| VcmdDQ.D | VcmdDQ.f32D | 0 | 0.1 | -3276.8 | 3276.7 | V
| VcmdDQ.Q | VcmdDQ.f32Q | 0 | 0.1 | -3276.8 | 3276.7 | V
0x1A99ssdd | DabcOrig.A | DabcOrig.f32A | 0 | 0.001 | -32.768 | 32.767 | p.u.
| DabcOrig.B | DabcOrig.f32B | 0 | 0.001 | -32.768 | 32.767 | p.u.
| DabcOrig.C | DabcOrig.f32C | 0 | 0.001 | -32.768 | 32.767 | p.u.
| ThetaPLL | ThetaPLL.f32theta | 0 | 0.01 | -327.68 | 327.67 | rad
0x1A9Assdd | Icmd.D | Icmd.f32D | 0 | 0.1 | -3276.8 | 3276.7 | A
| Icmd.Q | Icmd.f32Q | 0 | 0.1 | -3276.8 | 3276.7 | A
| IacRegErr.D | g_sIacRegCrVlpiGain.f32ErD | 0 | 0.1 | -3276.8 | 3276.7 | A
| IacRegErr.Q | g_sIacRegCrVlpiGain.f32ErQ | 0 | 0.1 | -3276.8 | 3276.7 | A
0x1A9Bssdd | VgridLN.A | VgridLN.f32A | 0 | 0.1 | -3276.8 | 3276.7 | V
| VgridLN.B | VgridLN.f32B | 0 | 0.1 | -3276.8 | 3276.7 | V
| VgridLN.C | VgridLN.f32C | 0 | 0.1 | -3276.8 | 3276.7 | V
| VgridMagPLL | VgridMagPLL | 0 | 0.1 | -3276.8 | 3276.7 | V
Bode sweep variable default, factor and range
Node | name | variable | default | factor | min | max | unit
0x1A9Cssdd | magic | 0xB0DE (header marker) | 0 | 1 | 0 | 65535
| u16PointCount | g_sBodeData.u16PointCount | 0 | 1 | 0 | 65535
| log10(fMin) | g_sBodeCfg.f32FMin | 0 | 0.001 | -32.768 | 32.767 | log10(Hz)
| log10(fMax) | g_sBodeCfg.f32FMax | 0 | 0.001 | -32.768 | 32.767 | log10(Hz)
0x1A9Cssdd | log10(freq) | g_sBodeData.f32FLogArray | 0 | 0.001 | -32.768 | 32.767 | log10(Hz)
| gain_dB | g_sBodeData.f32GaArray | 0 | 0.1 | -3276.8 | 3276.7 | dB
| phase_deg | g_sBodeData.f32PhArray | 0 | 0.1 | -3276.8 | 3276.7 | deg
| pointIndex | s_u16BodeSentPt | 0 | 1 | 0 | 65535

## RX CAN-B
Node | comment | byte0 | byte1 | byte2 | byte3 | byte4 | byte5 | byte6 | byte7
0x1A86xxxx | ACU grid voltage response | Grid LN Alpha (hi) | Grid LN Alpha (lo) | Grid LN Beta (hi) | Grid LN Beta (lo) | PCS LN Alpha (hi) | PCS LN Alpha (lo) | PCS LN Beta (hi) | PCS LN Beta (lo)

## TX CAN-B
Node | Comment | byte0 | byte1 | byte2 | byte3 | byte4 | byte5 | byte6 | byte7
0x1810A9ss | Grid voltage request to ACU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0